002

REVIEW STATUS

A - REVIEWED; WORK MAY PROCEED

B - REVIEWED WITH COMMENTS; REVISE & RESUBMIT;

WORK MAY PROCEED SUBJECT TO INCORPORATION OF

COMMENTS

C - OBJECTION - REVISE & RESUBMIT; WORK MAY

NOT PROCEED

D - REJECTED

E - REVIEW NOT REQUIRED; WORK MAY PROCEED

001

IT LAN-TCP/IP

ETHERNET

SWITCH/ROUTER (TYP.)

BACNet

BUILDING/NETWORK CONTROLLER

BACNet / LON OR MODBUS GATEWAY

BACNet

BUILDING/NETWORK CONTROLLER

CONNECTION

LON OR MODBUS 
BUILDING /NETWORK 
CONTROLLER

BMS WORKSTATION/SERVER MANAGEMENT LEVEL

MS/TP - DAISY CHAIN

MS/TP - DAISY CHAIN CONNECTION

BMS WORKSTATION OPERATION LEVEL (LIMITED FUNCTIONALITY)

BACNet ADVANCE 
APPLICATION 
CONTROLLER

BACNet ADVANCE 
APPLICATION 
CONTROLLER

UP TO 31 Nos

MS/TP - DAISY CHAIN CONNECTION

LIGHTING

AHU

FCU

BACNet ADVANCE 
APPLICATION 
CONTROLLER

BACNet ADVANCE 
APPLICATION 
CONTROLLER

LON OR MODBUS 
ADVANCE APPLICATION 
CONTROLLER

UP TO 31 Nos

BACNet ADVANCE 
APPLICATION 
CONTROLLER

OPTION 3 : GLOBAL CONNECTION BETWEEN DDC VIA TCP/IP FOR BACNet COMPLIANCE CONTROLLERS

STARTER / VFD

LON OR MODBUS 
ADVANCE APPLICATION 
CONTROLLER

UP TO 31 Nos

NOTE: THREE(3) OPTION ARE INDICATED FOR THE INTER CONNECTION OF NEGATIVE SOLATON ROOM EXHAUST TO THE SUPPLY AHU THE AHU NEEDS TO TURN OFF IN ANY CASE THAT THE EXHAUST FAN TURNS OFF TO AVOID PRESSURIZING THE ROOM AND SPREADING THE DISEASE

VAV

FLOW SWITCH / DIFF. 
SENSOR/ OR PRESS. 
SENSOR

LON OR MODBUS 
ADVANCE APPLICATION 
CONTROLLER

LIGHTING

EQUIPMENT BACNet FIELD DEVICES 
AND APPLICATION SPECIFIC 
CONTROLLER (TYP. TO ALL ASC)

BACNet ADVANCE 
APPLICATION 
CONTROLLER

OPTION 2 : DIGITAL INPUT TO THE DDC

NEGATIVE ISOLATION EXHAUST FAN

UP TO 31 Nos

AHU

S ARTER / VFD

OPTION 1 : ELECTRO MECHANICAL NETWORK

LON OR MODBUS 
ADVANCE APPLICATION 
CONTROLLER

FCU

VAV

NEGATIVE ISOLATION ROOM AHU

NEGATIVE ISOLATION ROOM

EQUIPMENT LON OR MODBUS FIELD 
DEVICES AND APPLICATION SPECIFIC 
CONTROLLER (TYP. TO ALL ASC)

001

27/03/19 BORDER CHANGED AND ISSUED FOR USE

000

24/01/18 ISSUED FOR USE

REV. No

DATE

REASON FOR ISSUE

DRAWING STATUS

ISSUED FOR USE

KINGDOM OF SAUDI ARABIA	ةیدوعسلا ةیبرعلا ةكلمملا

PROJECT REFERENCE -

STANDARD DRAWING

XXX

FACILITY No.

PROJECT TITLE 1

BMS AND MECHANICAL

ARABIC TITLE

ARABIC TITLE

INTEGRATION BLOCK

X

CONTRACT No.

PROJECT TITLE 2

DIAGRAM

PROJECT TITLE 3

SCALE

REV

DRAWING No.

SHEET 1 OF 1

EPM-KEE-13-000003

NTS