| PROJECT NAME: |  |  | DRAWING NO. |  |  |  |  | REV. |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. | QUESTIONS |  |  | ORIGINATOR |  |  | CHECKER |  |  |  |
|  |  |  |  | N/A | YES | NO | N/A |  | YES | NO |
| A. Drawing Presentation |  |  |  |  |  |  |  |  |  |  |
|  | Does Drawing comply with the project CAD Standards (All lines, symbols, legends, abbreviations, text, etc. are legible)? |  |  |  |  |  |  |  |  |  |
|  | Is the Drawing reviewed for constructability? |  |  |  |  |  |  |  |  |  |
|  | Is the layout prepared with the latest Architectural Layout? |  |  |  |  |  |  |  |  |  |
|  | Are the fields in the title block consistent with the project drawing log/index? |  |  |  |  |  |  |  |  |  |
|  | Key plan and North arrow are provided & the key plan shall have the layout area hatched. |  |  |  |  |  |  |  |  |  |
|  | Match lines or X-Y Grid are clearly defined. |  |  |  |  |  |  |  |  |  |
|  | Drawing notes are complete and agree with information on the drawings & details. |  |  |  |  |  |  |  |  |  |
|  | Are the layout dimensions (mounting height, operating height of the outlets, etc.) clearly defined? |  |  |  |  |  |  |  |  |  |
|  | Are the layout legends specific or provide the details regarding the type of the cables (Both the horizontal and vertical), mounting height of the voice and data outlets, rack and patch panel, patch card, etc.? |  |  |  |  |  |  |  |  |  |
|  | Bar scale is shown on the drawing and correct scale is used for all details, plan/elevation/sections. Details Not to Scale are also clearly marked. |  |  |  |  |  |  |  |  |  |
|  | All interdisciplinary comments and comments from previous revisions have been resolved and incorporated. Holds and revisions are correctly marked. |  |  |  |  |  |  |  |  |  |
|  | Limits of existing and new work including future expansions, interface points, battery limits are clearly defined. |  |  |  |  |  |  |  |  |  |
|  | Check if conduit continuations between drawings have been verified and properly identified. |  |  |  |  |  |  |  |  |  |
| B. Code/Standard/Project Specification |  |  |  |  |  |  |  |  |  |  |
|  | The type/size of wiring meets applicable code/standard and project specification. |  |  |  |  |  |  |  |  |  |
|  | Do the devices, components and the control panels as per NEMA standard and UL Listed? |  |  |  |  |  |  |  |  |  |
|  | Does the layout provide the installation detail of the controller, reader, locking devices, door position switch, request to exit (Push button), the power supply requirement, etc.? |  |  |  |  |  |  |  |  |  |
|  | Are identification and labelling provided as per codes and standards? |  |  |  |  |  |  |  |  |  |
| C. Reference Information |  |  |  |  |  |  |  |  |  |  |
|  | Check to ensure general notes include reference to applicable Codes, Standards and Project Specifications/Supplier submittals |  |  |  |  |  |  |  |  |  |
|  | Check for correctness of reference drawings. |  |  |  |  |  |  |  |  |  |
|  | Sections and details are correctly cross-referenced. |  |  |  |  |  |  |  |  |  |
| D. Design |  |  |  |  |  |  |  |  |  |  |
|  | Do the designing of Access Control System and the layout compatible with the existing advance new technology and the project requirements? |  |  |  |  |  |  |  |  |  |
|  | Have the layout coordinated with the Architectural/Structural Layout, Electrical and Mechanical System? |  |  |  |  |  |  |  |  |  |
|  | Do the system and layout covers entire building premises and protect the unauthorized access? |  |  |  |  |  |  |  |  |  |
|  | Do the system zone configuration as per the building life safety plan? (Ensure the zonal configurations are not as per the software program). |  |  |  |  |  |  |  |  |  |
|  | Do the designing of the system and the preparation of the layout as per IP Based System? |  |  |  |  |  |  |  |  |  |
|  | Have the layout specified the dedicated containment for the Access Control System? |  |  |  |  |  |  |  |  |  |
|  | Does the layout provide the detail of the containment route (both the horizontal and vertical)? |  |  |  |  |  |  |  |  |  |
|  | Do the selection and the location of peripheral devices, components and panels as per the specialist recommendation and the project requirements? |  |  |  |  |  |  |  |  |  |
|  | Do the Access Control System panels located inside the Telecom Room in each floor? |  |  |  |  |  |  |  |  |  |
|  | Do the layout provided the detail of the controller (main and slave controller) and associated software? |  |  |  |  |  |  |  |  |  |
|  | Do the system define the mode of the communications (TCP/IP) between controller and the panel? |  |  |  |  |  |  |  |  |  |
|  | Do the layout provide the details of the locking device and selection as per the specialist requirements (Door Strike Electric Lock - Fail Secure Lock, Fail Safe Lock and Magnetics)? |  |  |  |  |  |  |  |  |  |
|  | Do the layout provide the details and the type of the Reader (Example, Card Reader, Biometrics - Example: finger print, palm scan, hand geometric, iris scan, signature dynamic, keyboard dynamic, voice print, facial scan, hand topography, etc.)? |  |  |  |  |  |  |  |  |  |
|  | Do the system describes the two-way communication (high security) interface between Reader and Legacy Panels? |  |  |  |  |  |  |  |  |  |
|  | Do the system describes the function of the Proximity Reader and the detail of the communication radio frequency (125kHz or 13.56 MHz)? |  |  |  |  |  |  |  |  |  |
|  | Did the system consider the special functions like Anti-Pass Back, Elevator Control, Mantrap, Multifactor Authentication, etc.? |  |  |  |  |  |  |  |  |  |
|  | Does the system describe the requirement of the power source or power supply? (Please note and ensure that the power supply for the Access Control System shall feed from UPS Power). |  |  |  |  |  |  |  |  |  |
|  | Do the access control system designed and made provision to integrate with the existing system, Fire Alarm System and Life Safety System (CCTV network, intercom system, intrusion detection system, etc.)? |  |  |  |  |  |  |  |  |  |
|  | Are the layout provided the details of Operated Client workstation? |  |  |  |  |  |  |  |  |  |
|  | Do the system designed with override of fire/trouble condition if the door entry or telephone system override the door latch for operation? |  |  |  |  |  |  |  |  |  |
|  | Do Network Control & Management System and the Database Storage capacities are as per the project requirements? |  |  |  |  |  |  |  |  |  |
| No. | Reviewer's Comments (against each SLD) | Resolution |  |  |  |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |  |  |  |