| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | Preparation for Firing |  |  |  |  |  |  |
|  | Check that the boiler is filled with water to the appropriate level, and is vented, and the condition of water is chemically correct. |  |  |  |  |  |  |
|  | Check that the main valve in the main steam distribution header is closed. |  |  |  |  |  |  |
|  | Check that all water feed isolation valve and fuel line isolation valve are all open. |  |  |  |  |  |  |
|  | Air vents on the boiler shell are open. |  |  |  |  |  |  |
|  | Check that the main boiler stop valve and drain valves are closed for the level and alarm controls. |  |  |  |  |  |  |
|  | Check that the feed check valve and the isolation valves to the water level controls and the alarm and the feed pumps are open. |  |  |  |  |  |  |
|  | Check blowdown valve fully closed. |  |  |  |  |  |  |
|  | Check the electrical supplies are available at the boiler control panel and the feed system is available for immediate use. |  |  |  |  |  |  |
|  | Check the operation of the water level controller by allowing the feed water pump to run until switched off by the water level controller. Open the blowdown valve and check that the pump restarts at correct level. Close the blowdown valve afterwards. |  |  |  |  |  |  |
|  | Check the operation of the high level alarm by isolating the water level controller and opening its drain valve. The high level alarm should sound when the water level has raised the pre-set condition. Open the isolating valve on the level controller and close the drain valve afterwards. |  |  |  |  |  |  |
|  | Check the operation of the low level alarm by opening the blow down valve. The low level alarm should sound at low water level. Refill the tank with water and repeat the low level alarm test, the burner lock out at the second low level alarm should be activated. |  |  |  |  |  |  |
|  | Check that the water level in the blow-down vessel is satisfactory and that the vent is adequate. |  |  |  |  |  |  |
|  | Ensure that steam loads are available to check performance of the boiler. |  |  |  |  |  |  |
|  | Mains power to motors and controllers appropriate and accepted by Client Representatives. |  |  |  |  |  |  |
|  | Performance Testing |  |  |  |  |  |  |
|  | Speed governor shall regulate engine not to have more than 10% speed difference between shut off and maximum load (150% of the rated flow). |  |  |  |  |  |  |
|  | Speed verification switch shall be tested to increase engine speed and to shut down when speed exceeds 120% of the rated speed. Reset manually in the engine instrument panel to restart the engine. |  |  |  |  |  |  |
|  | Battery in good condition including charger. |  |  |  |  |  |  |
|  | Engine heater operating normally when engine is off (as applicable). |  |  |  |  |  |  |
|  | No apparent visible air leakage from the exhaust system. |  |  |  |  |  |  |
|  | Starting with the system in static, water is released to reduce the system pressure. The system response shall be confirmed as follows: - Jockey pump starts at set cut-in pressure (JP set pressure is higher than lead FP set pressure but lower than system pressure). Record JP start pressure and turn off power to the JP. Water is again release to test lead FP cut-in pressure: - Lead FP starts at set cut-in pressure (Lead FP cut-in pressure is higher than lag FP (diesel normally). Record Lead FP cut-in pressure and turn off power to Lead FP. Water is again release to test lag FP cut-in pressure: - Lag FP starts at set cut-in pressure (Lag FP cut-in pressure is the lowest pressure allowable for the sprinklers to operate at minimum operating pressure (normally 75 psig). |  |  |  |  |  |  |
|  | No hunting (controller turning on and off pump) during system test. |  |  |  |  |  |  |
|  | Running Period Timers set at 10 mins. minimum automatically turns off pumps when system pressure returns to normal (as applicable when controllers are equipped with RPT for automatic shut-off of fire pumps). |  |  |  |  |  |  |
|  | Pump controller was able to retain set pressure for variable speed drive fire pumps (as applicable) as per manufacturer methodology to prove proper operation of VFD driven pumps. |  |  |  |  |  |  |
|  | Pumps continue to run when system pressure returns to normal for manual shut off controllers (as applicable). |  |  |  |  |  |  |
|  | Alarm gong shall activate during water flow (as applicable). |  |  |  |  |  |  |
|  | Contractor shall submit the fill-up Acceptance Test Form required by NFPA 20. |  |  |  |  |  |  |
|  | Note that for jockey pump, refer to pump functional test checklist. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |