| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | FUNCTIONAL CHECK |  |  |  |  |  |  |
|  | Fan air flow and ESP matches compare to fan performance curve at 0%, 50% and 100% flow. |  |  |  |  |  |  |
|  | Supply voltage to the fan appropriate compared to the rated voltage at rated capacity. |  |  |  |  |  |  |
|  | Current drawn by fan motors does not exceed rated current. |  |  |  |  |  |  |
|  | Fan rotation correct. |  |  |  |  |  |  |
|  | Rotational speed for the fan correct compared to the equipment nameplate. |  |  |  |  |  |  |
|  | Fan has no unusual noise or vibration. |  |  |  |  |  |  |
|  | Suction damper stroke fully without binding and spans calibrated. |  |  |  |  |  |  |
|  | The HOA switch properly activates and deactivates the unit. |  |  |  |  |  |  |
|  | Supply air duct static pressure sensor is located 2/3rds down longest supply duct in duct and not subject to turbulence from elbows, vanes, etc. (as applicable for VFD drive fan): - Record location of sensor - Record sensor reading at BMS - Verify sensor setpoint from TAB Report. |  |  |  |  |  |  |
|  | Fan flow or differential pressure sensor mapped correctly to BMS: Verify alarm at BMS upon flow failure. |  |  |  |  |  |  |
|  | Fan VFD speed reporting reliable values (as applicable): - Record reading at BMS - Record VFD Hz at minimum and maximum. |  |  |  |  |  |  |
|  | Fan airflow monitoring station reporting reliable values (as applicable): - Record reading at BMS - Record supply airflow with all terminal units at maximum airflow - Record supply airflow with all terminal units at minimum airflow. |  |  |  |  |  |  |
|  | Fan flow graphic is correct in BMS: - Graphic easily displays system On/Off. |  |  |  |  |  |  |
|  | Specified sequences of operation and operating schedules have been implemented with all variations documented (as applicable). |  |  |  |  |  |  |
|  | Specified point-to-point checks have been completed and documentation record submitted for this system. All alarm points have been tested and confirmed. |  |  |  |  |  |  |
|  | EQUIPMENT PERFORMANCE CHECK |  |  |  |  |  |  |
|  | Adjust measured flowrate and head if rotational speed measured differs greatly with the rated rpm using fan affinity law formula. Calculate the air power using the flowrate and head. |  |  |  |  |  |  |
|  | Take current drawn during testing of rated capacity and head. Record voltage for the phases and calculate the electrical power drawn. |  |  |  |  |  |  |
|  | Calculate the overall efficiency of the fan and motor assembly by dividing the air power with the electrical power. Calculated total efficiency of the fan+motor assembly shall be equal or greater compare to the manufacturer rated total efficiency of the assembly. |  |  |  |  |  |  |
|  | SYSTEM PERFORMANCE CHECK |  |  |  |  |  |  |
|  | Verify scheduling of unit on BMS in Occupied Mode: - Verify fans are on as per schedule. Put fan in off manually; verify alarm at BMS upon fan failure. |  |  |  |  |  |  |
|  | Adjust supply duct static pressure setpoint. Allow unit to stabilize. Verify fan speed modulates to maintain static pressure setpoint. Verify airflow monitoring station modulates accordingly: - Record BMS static pressure setpoint - Record static pressure setpoint adjustments made for testing - Record airflow variation. |  |  |  |  |  |  |
|  | Override suction air damper to 0%, start unit from unoccupied. Verify supply fan does NOT start unit. |  |  |  |  |  |  |
|  | Verify when fan is off, suction dampers are closed. |  |  |  |  |  |  |
|  | Create smoke detection alarm at smoke detector wiring. Verify BMS and FDAS alarm is generated. Verify fans are OFF, outdoor air damper is CLOSED when smoke is detected. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |