| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | FUNCTIONAL CHECK |  |  |  |  |  |  |
|  | Supply fan air flow and ESP matches compare to fan performance curve at 100% flow. |  |  |  |  |  |  |
|  | Supply voltage to the supply fan appropriate compared to the rated voltage at rated capacity. Voltage imbalance between phases within acceptable limits. |  |  |  |  |  |  |
|  | Current drawn by supply fan motors does not exceed rated current. |  |  |  |  |  |  |
|  | Supply fan rotation correct. |  |  |  |  |  |  |
|  | Rotational speed for the supply fan correct compared to the equipment nameplate. |  |  |  |  |  |  |
|  | Supply fan has no unusual noise or vibration. |  |  |  |  |  |  |
|  | All dampers (supply and return) stroke fully without binding and spans calibrated. |  |  |  |  |  |  |
|  | Cooling valves stroke fully and easily, and spanning is calibrated. |  |  |  |  |  |  |
|  | Valves verified to not be leaking through coils when closed at normal operating pressure. |  |  |  |  |  |  |
|  | CRAC monitoring station reporting reliable values: - Record status (On/Off) at BMS - Record actual site status. |  |  |  |  |  |  |
|  | Room temperature and humidity monitoring station reporting reliable values: - Record temperature and %RH values at BMS - Record actual site instrument reading for temperature and %RH. |  |  |  |  |  |  |
|  | CRAC flow graphic is correct in BMS: - Graphic easily displays system On/Off. |  |  |  |  |  |  |
|  | Specified point-to-point checks have been completed and documentation record submitted for this system. All alarm points have been tested and confirmed. |  |  |  |  |  |  |
|  | EQUIPMENT PERFORMANCE CHECK |  |  |  |  |  |  |
|  | Adjust measured flowrate and TSP (Total Static Pressure) if rotational speed measured differs greatly with the rated rpm using fan affinity law formula. Calculate the air power using the flowrate and TSP. TSP is ESP (external static pressure drop+ pressure drop across the CRAC which includes filters and coils). |  |  |  |  |  |  |
|  | Take current drawn during testing of rated capacity and TSP. Record voltage for the phases and calculate the electrical power drawn. Ensure that heater for humidification and heater for humidity control (for high latent load) is not activated by temporary removing electrical connections. Restore connection once current reading is completed. |  |  |  |  |  |  |
|  | Calculate the overall efficiency of the fan and motor assembly by dividing the air power with the electrical power. Calculated total efficiency of the fan+motor assembly shall be equal or greater compare to the manufacturer rated total efficiency of the assembly. |  |  |  |  |  |  |
|  | Measure on-coil and off-coil air temperature and %RH and calculate the cooling coil capacity by the measured air flowrate and enthalpy taken from the Psychrometric chart. Calculated cooling capacity must be close to the manufacturer published adjusted cooling rating based on actual condition. |  |  |  |  |  |  |
|  | To test humidification water heater, increase humidity set-point to 60%RH. Heater should be activated. Take current readings. |  |  |  |  |  |  |
|  | For unit equipped with air heater for humidification control for high latent load, it will require steam or water source. Once steam is injected, air heater should activate. Take current readings. |  |  |  |  |  |  |
|  | SYSTEM PERFORMANCE CHECK |  |  |  |  |  |  |
|  | Create smoke detection alarm at smoke detector wiring. Verify FDAS alarm is generated thru the Clean Agent Control Panel. Verify CRAC is OFF when smoke is detected (applicable for non-healthcare Data Room). |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |