| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | FUNCTIONAL CHECK |  |  |  |  |  |  |
|  | Pump flowrate and head matches with the pump performance curve at 0%, 50%, and 100% flow. |  |  |  |  |  |  |
|  | Supply voltage to the pump appropriate compared to the rated voltage. Voltage imbalance between phases within acceptable limits. |  |  |  |  |  |  |
|  | Current drawn by the pump motor does not exceed rated current. |  |  |  |  |  |  |
|  | Pump rotation correct. |  |  |  |  |  |  |
|  | Rotational speed for the pump as per the nameplate correct. |  |  |  |  |  |  |
|  | Pump has no unusual noise or vibration during operation. |  |  |  |  |  |  |
|  | No cavitation observed when pumps are running. |  |  |  |  |  |  |
|  | The HOA switch properly activates and deactivates the unit. |  |  |  |  |  |  |
|  | In auto position, pumps are staging based on cut-in and cut-off level of magnetic-activated level switches installed in the condensate tank for lead and lag pump. |  |  |  |  |  |  |
|  | High level and low level alarm functional test conducted by manually lifting and releasing float of the magnetic-activated level switch. |  |  |  |  |  |  |
|  | EQUIPMENT PERFORMANCE CHECK |  |  |  |  |  |  |
|  | Adjust measured flowrate and head if rotational speed measured differs greatly with the rated rpm using pump affinity law formula. Calculate the water power using the flowrate and head. |  |  |  |  |  |  |
|  | Take current drawn during testing of rated capacity and head. Record voltage for the phases and calculate the electrical power drawn. |  |  |  |  |  |  |
|  | Calculate the overall efficiency of the pump and motor assembly by dividing the water power with the electrical power. Calculated total efficiency of the pump+motor assembly shall be equal or greater compare to the manufacturer rated total efficiency of the assembly. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |