| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | FUNCTIONAL CHECK |  |  |  |  |  |  |
|  | Fan air flow matches to the approved manufacturer documents. |  |  |  |  |  |  |
|  | Supply voltage to the fan appropriate compared to the rated voltage. Voltage imbalance between phases within acceptable limit. |  |  |  |  |  |  |
|  | Current drawn by fan motors does not exceed rated current at rated capacity. |  |  |  |  |  |  |
|  | Fan rotation correct. |  |  |  |  |  |  |
|  | Rotational speed for the fan correct compared to the equipment nameplate. |  |  |  |  |  |  |
|  | Fan has no unusual noise or vibration. |  |  |  |  |  |  |
|  | The HOA switch properly activates and deactivates the unit (for VFD Drive CT). |  |  |  |  |  |  |
|  | Fan speed modulates (increase or decrease) to maintain condenser water temperature to 85°F (for VFD drive CT). |  |  |  |  |  |  |
|  | For multiple CT, staging of CT is proven by closing motorized valve to CT and turning off-fan when further decrease in load is required while all CT fan motor are at minimum allowable frequency (usually 15 to 18Hz). |  |  |  |  |  |  |
|  | No water over-flowing on basin during staging and de-staging of Cooling Towers. Water level is maintained within limit as per manufacturer’s instruction. |  |  |  |  |  |  |
|  | No vortex formed in CT basin. |  |  |  |  |  |  |
|  | Water is evenly sprinklered or loaded across the CT fill. No excessive overlapping of loading area which reduces water to air contact (fill performance) in the cellular fill media. |  |  |  |  |  |  |
|  | No excessive water loading to the walls of the CT which result in lower cellular media water to air contact. |  |  |  |  |  |  |
|  | Correct water spray nozzle provided. |  |  |  |  |  |  |
|  | Make-up water and float valve (or motorized valve and level switches) properly functioning. |  |  |  |  |  |  |
|  | Low and high level water alarms functional. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |