| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | Electric Elevators |  |  |  |  |  |  |
|  | Electric traction elevators shall be tested according to ASME A.17.1 Category 1 and Category 5 in the presence of Certified Third Party Testing Agency. Category 1 Testing (No Load and Low Speed) comprise of: - Oil Buffers according to Section 8.11.2.2.1 - Car and Counterweight Safety System according to Section 8.11.2.2.2 - Speed Governors according to Section 8.11.2.2.3 - Slack-rope Devices on Winding Drum Machines according to Section 8.11.2.2.4 - Normal and Final Terminal Stopping Devices according to Section 8.11.2.2.5 - Fire Fighter’s Emergency Operation according to Section 8.11.2.2.6 - Emergency Power Operation according to Section 8.11.2.2.7 - Power Operation of Door System according to Section 8.11.2.2.8 - Broken Rope, Tape, or Chain Switch according to Section 8.11.2.2.9 - Electrical Protective Devices according to Section 8.11.2.2.10 Category 5 Testing (Rated Load and Rated Speed) comprise of: - Car and Counterweight Safety System according to Section 8.11.2.3.1 - Speed Governors according to Section 8.11.2.3.2 - Oil Buffers according to Section 8.11.2.3.3 - Braking System and braking distance according to Section 8.11.2.3.4 - Emergency Power Operation according to Section 8.11.2.3.5 - Emergency Terminal Stopping and Speed Limiting Device according to Section 8.11.2.3.6 - Power Opening of Doors according to Section 8.11.2.3.7 - Levelling Zone and Levelling Speed according to Section 8.11.2.3.8 - Inner Landing Zone according to Section 8.11.2.3.9 - Emergency Stopping Devices according to Section 8.11.2.3.10. |  |  |  |  |  |  |
|  | For electric traction elevator with emergency power system and permitted to carry passengers, shall be tested at 125% of the rated load at rated speed according to ASMEA.17.1 |  |  |  |  |  |  |
|  | All electrical installation and testing shall conform to NFPA 70 and ASME requirements inclusive of overloads. |  |  |  |  |  |  |
|  | Fireman’s service phase I and Phase II recall tested with the FDAS System. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |