| PROJECT NAME: |  |  |  |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. |  | INSPECTION ITEM |  |  |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  |  |  |  | N/A | YES |  | NO |
|  |  | General |  |  |  |  |  |  |  |  |
|  |  | Escalators and Moving Walks shall be tested according to ASME A.17.1 Category 1 (no load) in the presence of Certified Third Party Testing Agency. Category 1 Testing is composed of the following test: - Machine Space accessibility as per Section 8.11.4.2.1 - Stop Switch operation test as per Section 8.11.4.2.2 - Controller and wiring functionality test as per Section 8.11.4.2.3 - Drive machine and brake test including braking distance as per Section 8.11.4.2.4 - Speed Governor test to shut-down if speed increase/decrease more than 120% as per Section 8.11.4.2.5 - Broken Drive Chain Device safety test as per Section 8.11.4.2.6 - Reversal Stop Switch testing as per Section 8.11.4.2.7 - Broken Step Chain or Treadway Device test as per Section 8.11.4.2.8 - Step Up thrust Device testing as per Section 8.11.4.2.9 - Missing Step or Pallet Device testing as per Section 8.11.4.2.10 - Step or Pallet Level Device testing as per Section 8.11.4.2.11 - Step, Pallet, Step or Pallet Chain, and trusses structural soundness test as per Section 8.11.4.2.12 - Handrail Safety Systems test as per Section 8.11.4.2.13 - Heater testing (as required) as per Section 8.11.4.2.14 - Permissible Stretch in escalator chain safety test as per Section 8.11.4.2.15 - Response to smoke detector test as per Section 8.11.4.2.16 - Comb-Step or Comb-Pallet Impact Device test as per Section 8.11.4.2.17 - Step/Skirt Performance Index testing as per Section 8.11.4.2.18 - Clearance between Step and Skirt (loaded gap) as per Section 8.11.4.2.19 - Inspection of Control Devices as per Section 8.11.4.2.20 - u. Step Lateral Displacement Device test as per Section 8.11.4.2.21 |  |  |  |  |  |  |  |  |
|  |  | All electrical installation and testing shall conform to NFPA 70 and ASME requirements inclusive of overloads, electrical ratings, insulation resistance, earthing resistance, etc. |  |  |  |  |  |  |  |  |
|  |  | Escalators tested for 15 minutes forward or up direction and another 15 minutes backward or down direction continuously without any deficiencies. |  |  |  |  |  |  |  |  |
| No. | Reviewer's Comments |  |  |  | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  |  |  |  | Checker's Name / Signature and Date: |  |  |  |  |  |