| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General |  |  |  |  |  |  |
|  | Identification record of each capacitor bank such as Manufacturer’s name, serial number, year of manufacture, rated and measured capacitance, rated output, rated voltage, rated current, temperature category and di-electric fluid type has been provided. |  |  |  |  |  |  |
|  | Identification record of any tuning reactor such as Manufacturer’s name, serial number, year of manufacture, rated reactance, rated voltage and rated current has been provided. |  |  |  |  |  |  |
|  | Discharge test has been carried out for capacitors build to IEC 60871. Discharge voltage shall be 75V or less from initial peak voltage of √2 Un (Un is the rated voltage) within 10 mins. discharge time. |  |  |  |  |  |  |
|  | Discharge test has been carried out for capacitors build to AS 2897. Discharge voltage shall be 50V or less from initial peak voltage of √2 Un (Un is the rated voltage) within 5 mins. discharge time for Un≤ 25 kV. Discharge voltage shall be 75V or less from initial peak voltage of √2 Un (Un is the rated voltage) within 10 mins. discharge time for Un≥ 25 kV. |  |  |  |  |  |  |
|  | Insulation resistance test has been conducted and yield acceptable test results. |  |  |  |  |  |  |
|  | Capacitance test has been conducted and yield acceptable test results. |  |  |  |  |  |  |
|  | High voltage withstand test has been conducted on capacitors (as applicable). |  |  |  |  |  |  |
|  | Balance check of each capacitor bank has been conducted. |  |  |  |  |  |  |
|  | Primary injection test conducted to check balance between banks (as applicable). |  |  |  |  |  |  |
|  | Load test conducted immediately on all protection and metering circuits after energization. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |