| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | Functional Test for On-line UPS |  |  |  |  |  |  |
|  | Phase rotation testing conducted and passed. |  |  |  |  |  |  |
|  | All other electrical pre-start testing (insulation resistance, continuity, battery testing, etc.) conducted and passed. |  |  |  |  |  |  |
|  | Primary power has been applied and stable for 3 days without any noticeable malfunction for the UPS and its control and monitoring system. |  |  |  |  |  |  |
|  | Load testing shall be conducted with the use of capacitor banks. Run down time shall be proven including battery back-up as well as charging time as specified in the design/manufacturer. |  |  |  |  |  |  |
|  | Transfer switch and by-pass tested without any foreseen problems (flickering, brown-out, black-out, etc.). |  |  |  |  |  |  |
|  | Alarm system tested including overrides. |  |  |  |  |  |  |
|  | System testing for 30 days shall be conducted (UPS is in service for 30 days) prior to final acceptance. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |