| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General Check |  |  |  |  |  |  |
|  | No unpleasant smell around the WWT Plant. |  |  |  |  |  |  |
|  | All equipment current drawn are normal and no noticeable abnormalities observed. |  |  |  |  |  |  |
|  | Float valves, float switches, and motorized valves are properly working and controlling water levels. |  |  |  |  |  |  |
|  | Plant is producing the required treatment capacity (m3 per day) and water bacteriological analysis is within the acceptable parameter. |  |  |  |  |  |  |
|  | Equalization Tank |  |  |  |  |  |  |
|  | Incoming wastewater are filtered efficiently and all large materials are retained by trash trap, bar screen and comminutors. |  |  |  |  |  |  |
|  | Pumps and pretreatment blowers are operating and cycling properly. Flow to the treatment is regulated. |  |  |  |  |  |  |
|  | High and low level alarms are operating properly. |  |  |  |  |  |  |
|  | Aeration Tank |  |  |  |  |  |  |
|  | Aeration mixing is adequate and blower is visibly operating and properly cycling. Liquid appearance must be chocolate brown with minimal foaming. |  |  |  |  |  |  |
|  | Diffusers all open, no dead spots, and air flow balanced. |  |  |  |  |  |  |
|  | Liquid leaving Aeration Tank is clear with satisfactory smell. |  |  |  |  |  |  |
|  | Settling Tank |  |  |  |  |  |  |
|  | All equipment functioning with settling tank surface clean with clear effluent. |  |  |  |  |  |  |
|  | Skimmers are removing scums automatically on water surface. |  |  |  |  |  |  |
|  | Effluent free from excess foaming and solids. |  |  |  |  |  |  |
|  | Sludge return pump operating properly and cycling as per schedule. |  |  |  |  |  |  |
|  | Sides/hoppers wall scraped regularly. |  |  |  |  |  |  |
|  | Sludge Holding Tank |  |  |  |  |  |  |
|  | Properly used and operating for sludge wasting. |  |  |  |  |  |  |
|  | Sludge being hauled as needed. |  |  |  |  |  |  |
|  | Tertiary Filters |  |  |  |  |  |  |
|  | Operating properly with backwash pumps (for mechanical filtering). |  |  |  |  |  |  |
|  | Air blowers and aerator operating properly with no visible clogs and solid build up (filter ponds). |  |  |  |  |  |  |
|  | High-water alarm operating properly for filter/polishing ponds. |  |  |  |  |  |  |
|  | Chlorinator |  |  |  |  |  |  |
|  | Chlorine is properly injected and dozed. Equipment is operating properly. |  |  |  |  |  |  |
|  | Effluent Tank |  |  |  |  |  |  |
|  | Effluent appears clear and free of suspended solids and foaming. |  |  |  |  |  |  |
|  | Pumps are operating and cycling properly. |  |  |  |  |  |  |
|  | High level alarm properly functioning. |  |  |  |  |  |  |
|  | Perform necessary operational and control tests (settle ability test, pH, chlorine residual, etc.). |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |