| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General Installation |  |  |  |  |  |  |
|  | All equipment current drawn are within normal limits and no noticeable abnormalities observed. |  |  |  |  |  |  |
|  | Float valves, float switches, and motorized valves are properly working and controlling water levels. |  |  |  |  |  |  |
|  | Plant is producing the required treatment capacity (m3 per day) and water quality is within the acceptable contract parameter based on the raw water parameters considered. |  |  |  |  |  |  |
|  | Permeate flow and water recovery as per the approved documents based on the raw water quality (TDS), temperature, and pH considered. |  |  |  |  |  |  |
|  | All equipment (pumps and accessories) including controllers are individually tested and accepted. |  |  |  |  |  |  |
|  | Pre-Treatment |  |  |  |  |  |  |
|  | Feedwater temperature and pH is within the design range (25°C and 7.8pH). TDH is within acceptable limits. |  |  |  |  |  |  |
|  | Reject water flowrate as per the design recovery rate. |  |  |  |  |  |  |
|  | Feedwater pressure in compliance to the minimum pressure required by the equipment. |  |  |  |  |  |  |
|  | Pre-chlorination dosing system (pumps, control, and tanks) properly working. |  |  |  |  |  |  |
|  | Filter feed pump working properly including backwash function. |  |  |  |  |  |  |
|  | Pressure sand filter is operational and fully automatic including backwash function. |  |  |  |  |  |  |
|  | Carbon filter is operational and fully automatic including backwash function. |  |  |  |  |  |  |
|  | Anti-scalant dosing system (pumps and dozing tanks) operational. |  |  |  |  |  |  |
|  | Pipe and fittings has no visible leaks during operation and valves automatically isolates and direct flows. |  |  |  |  |  |  |
|  | All pressure gauges installed and readings does not exceed half of the dial reading. |  |  |  |  |  |  |
|  | Reverse Osmosis Plant |  |  |  |  |  |  |
|  | Cartridge filter in place. |  |  |  |  |  |  |
|  | High pressure pump properly working without excessive vibration and noise. |  |  |  |  |  |  |
|  | Reverse osmosis membrane installed according to the required number of elements and producing required flowrate. |  |  |  |  |  |  |
|  | Brine throttling control valve properly working. |  |  |  |  |  |  |
|  | Low pressure switch protection for the RO membrane properly working. |  |  |  |  |  |  |
|  | Conductivity meter installed and calibrated and results in within acceptable limits. |  |  |  |  |  |  |
|  | Flowmeter (rotameter) is within limit to indicate proper flow and velocity. |  |  |  |  |  |  |
|  | No visible leakage for the high pressure piping. |  |  |  |  |  |  |
|  | All pressure gauges installed and readings does not exceed half of the dial reading. |  |  |  |  |  |  |
|  | Clean in Place (CIP) installed inclusive of flushing tank and properly working (as required by the contract). |  |  |  |  |  |  |
|  | Collection tank installed complete with float switches and motorized valve properly working. |  |  |  |  |  |  |
|  | De-Ionization Plant |  |  |  |  |  |  |
|  | DI feed pumps properly working without excessive vibration and noise. |  |  |  |  |  |  |
|  | Separate Strong Acid Cation tank installed with resin provided as per manufacturer recommendation. |  |  |  |  |  |  |
|  | Separate Strong Base Anion tank installed with resin provided as per manufacturer recommendation. |  |  |  |  |  |  |
|  | Strong Base and Acid Regeneration System installed and properly working. |  |  |  |  |  |  |
|  | All controllers functional and properly working. |  |  |  |  |  |  |
|  | Final Filtration and Treatment |  |  |  |  |  |  |
|  | UV unit installed and properly working. UV unit turn-off in absence of flow. |  |  |  |  |  |  |
|  | Final filter installed with the correct type of cartridge (0.2 mic). |  |  |  |  |  |  |
|  | Perform necessary water analysis tests (pH and TDS). |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |