| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General Installation |  |  |  |  |  |  |
|  | General appearance good and no apparent damage. |  |  |  |  |  |  |
|  | Equipment label affixed and matches the equipment tagging in the as-build drawing. |  |  |  |  |  |  |
|  | Unit capacity and ratings indicated (KVAr, voltage, and amperage) and type of breakers (gas or vacuum) in the nameplate matches the capacity and ratings in the design and approved documents with derating factors considered. Date of manufacturing shall also be indicated. |  |  |  |  |  |  |
|  | Site is clean and tidy. |  |  |  |  |  |  |
|  | Location of unit and orientation correct as per drawing. |  |  |  |  |  |  |
|  | Check concrete pad and unit is bolted to pad properly. |  |  |  |  |  |  |
|  | All electrical warning and safety signs provided and in proper place. |  |  |  |  |  |  |
|  | Unit ventilation grids clear from any obstruction. |  |  |  |  |  |  |
|  | Locks installed and functional and door/lids in working order and swings freely. |  |  |  |  |  |  |
|  | Gas struts in good condition (applicable for SF6 insulated) and gas level is ok. |  |  |  |  |  |  |
|  | Doors and frames are earthed correctly. |  |  |  |  |  |  |
|  | Neutral/earth connection to standards. |  |  |  |  |  |  |
|  | Cables correctly terminated, labelled, and supported. |  |  |  |  |  |  |
|  | HV/MV bushing without any apparent damage. |  |  |  |  |  |  |
|  | All connections tight to relevant torque requirements. |  |  |  |  |  |  |
|  | Vermin proofing (conduits filled with foam fill and/or gland plates installed) provided. |  |  |  |  |  |  |
|  | Check that mounting frames are correctly bonded to the appropriate capacitor bushing as per the manufacturer drawing. No mounting frame should be floating. |  |  |  |  |  |  |
|  | Check all HV/MV equipment has specified phase to phase and phase to earth clearance. |  |  |  |  |  |  |
|  | Check earth switch and other isolator operation. Should be properly functioning. |  |  |  |  |  |  |
|  | Check operation of discharge timers and electrical interlocking with control system and HV/MV CB and switches capable of energizing the banks. |  |  |  |  |  |  |
|  | Check operation of point on wave (POW) relays, including adaptive capability of the POW relays. |  |  |  |  |  |  |
|  | Check mechanical interlocking system works correctly and that the instruction diagram showing operation of the system is fixed to the unit. |  |  |  |  |  |  |
|  | Ensure interlock system keys are provided. |  |  |  |  |  |  |
|  | Check cubicle lighting operation. |  |  |  |  |  |  |
|  | Check all fuses/links are in place. |  |  |  |  |  |  |
|  | Check all CT secondary links are closed. |  |  |  |  |  |  |
|  | Check VT are working properly. |  |  |  |  |  |  |
|  | Ensure that MSDS for capacitor di-electric fluid is on site. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |