| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General Installation |  |  |  |  |  |  |
|  | General appearance good and no apparent damage. |  |  |  |  |  |  |
|  | Equipment label affixed and matches the equipment tagging in the as-build drawing. |  |  |  |  |  |  |
|  | Breaker capacity and ratings indicated (voltage and amperage) and type (gas or vacuum) in the nameplate matches the capacity and ratings in the design and approved documents with derating factors considered. Date of manufacturing shall also be indicated. |  |  |  |  |  |  |
|  | Site is clean and tidy. |  |  |  |  |  |  |
|  | Location of unit and orientation correct as per drawing. |  |  |  |  |  |  |
|  | Check concrete pad and unit is bolted to pad properly. |  |  |  |  |  |  |
|  | All electrical warning and safety signs provided and in proper place. |  |  |  |  |  |  |
|  | Unit ventilation grids clear from any obstruction. |  |  |  |  |  |  |
|  | Locks installed and functional and door/lids in working order. |  |  |  |  |  |  |
|  | Gas struts in good condition (applicable for SF6 insulated). |  |  |  |  |  |  |
|  | Doors and frames are earthed correctly. |  |  |  |  |  |  |
|  | Neutral/earth connection to standards. |  |  |  |  |  |  |
|  | Vacant conduits capped. |  |  |  |  |  |  |
|  | Vermin proofing (conduits filled with foam fill and/or gland plates installed) provided. |  |  |  |  |  |  |
|  | Cables correctly supported. |  |  |  |  |  |  |
|  | Cable termination correctly labelled and identified including phasing and destination tags. Phasing heat shrink to be below termination. |  |  |  |  |  |  |
|  | HV/LV bushing without any apparent damage. |  |  |  |  |  |  |
|  | All connections tight to relevant torque requirements. |  |  |  |  |  |  |
|  | Check gas level is ok. |  |  |  |  |  |  |
|  | Check switch numbering/labelling is correct and installed properly. |  |  |  |  |  |  |
|  | Status indicator on switch correct. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |