| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | Main Busbar Mechanical Check and Visual Inspection |  |  |  |  |  |  |
|  | Verify the Bus bar sizes are as per the approved manufacturer schematic |  |  |  |  |  |  |
|  | Inspect for physical damage/defects. |  |  |  |  |  |  |
|  | Check bus arrangement for conformance with approved drawings. |  |  |  |  |  |  |
|  | Check tightness of all bolted connections (torque wrench method). |  |  |  |  |  |  |
|  | Check that all enclosure grounding is securely connected. |  |  |  |  |  |  |
|  | Inspect internal compartments for cleanliness (free from dust and moisture). |  |  |  |  |  |  |
|  | Check for watertight seals at all joints including expanding interface points. |  |  |  |  |  |  |
|  | Check bus conductor support insulators for cracked insulation chipped porcelain etc. |  |  |  |  |  |  |
|  | Check quality of paint work (inside and outside) |  |  |  |  |  |  |
|  | Check that ventilation openings are not blocked and screened against ingress of insects and rain. |  |  |  |  |  |  |
|  | Moisture drain holes available at bottom of enclosure. |  |  |  |  |  |  |
|  | Check anti-condensation heaters mounted at the correct locations (Bottom) |  |  |  |  |  |  |
|  | Main Busbar Electrical Check |  |  |  |  |  |  |
|  | Insulation resistance testing done and acceptable. |  |  |  |  |  |  |
|  | Contact resistance for joints and connections done and acceptable. |  |  |  |  |  |  |
|  | Insulated Case Circuit Breaker Mechanical Check |  |  |  |  |  |  |
|  | Insect for physical damage/defects. |  |  |  |  |  |  |
|  | Check quality of paintwork. |  |  |  |  |  |  |
|  | Check nameplate information for correctness. |  |  |  |  |  |  |
|  | Verify the circuit breakers ratings are as per the approved drawing |  |  |  |  |  |  |
|  | Check tightness of all bolted connections (torque wrench method). |  |  |  |  |  |  |
|  | Check racking mechanism for alignment and smoothness of operation. |  |  |  |  |  |  |
|  | Check operation of all mechanical interlocks. |  |  |  |  |  |  |
|  | Check for correct breaker position indication. |  |  |  |  |  |  |
|  | Check for correct spring status indication (spring charged/discharged). |  |  |  |  |  |  |
|  | For air magnetic breakers, check the arc chutes for damage and correct positioning above the interrupter contacts. |  |  |  |  |  |  |
|  | For minimum oil breakers, check correct oil level in each pole. |  |  |  |  |  |  |
|  | Perform all specific checks on the breaker and spring operating mechanism according to the manufacturer’s instructions. |  |  |  |  |  |  |
|  | Check that all control wiring is correct according to the approved drawings and terminal connections are secure. |  |  |  |  |  |  |
|  | Insulated Circuit Breaker Electrical Test |  |  |  |  |  |  |
|  | Contact resistance for joints and connections done and acceptable. |  |  |  |  |  |  |
|  | Timing Testing conducted and results are acceptable. |  |  |  |  |  |  |
|  | Current Transformer Mechanical Check |  |  |  |  |  |  |
|  | Inspect for physical damage/defects. |  |  |  |  |  |  |
|  | Check nameplate information for correctness. |  |  |  |  |  |  |
|  | Check that outdoor secondary wiring terminations are installed in moisture proof enclosures. |  |  |  |  |  |  |
|  | Check tightness of all bolted connections (torque wrench method). |  |  |  |  |  |  |
|  | Check that all grounding cables are securely connected. |  |  |  |  |  |  |
|  | Current Transformer Electrical Check |  |  |  |  |  |  |
|  | Polarity test conducted and results are acceptable. |  |  |  |  |  |  |
|  | Ratio test conducted and results are acceptable. |  |  |  |  |  |  |
|  | Excitation test conducted and results are acceptable. |  |  |  |  |  |  |
|  | Insulation resistance test conducted and results are acceptable. |  |  |  |  |  |  |
|  | Winding resistance test conducted and results are acceptable. |  |  |  |  |  |  |
|  | Burden test conducted and results are acceptable. |  |  |  |  |  |  |
|  | Voltage Transformer Mechanical Check |  |  |  |  |  |  |
|  | Inspect for physical damage/defects. |  |  |  |  |  |  |
|  | Check nameplate information for correctness. |  |  |  |  |  |  |
|  | Check tightness of all bolted connections (torque wrench method). |  |  |  |  |  |  |
|  | Check that the HV connection does not transfer stress to the VT HV terminal. |  |  |  |  |  |  |
|  | Check that all grounding cables are securely connected. |  |  |  |  |  |  |
|  | Check mechanical clearances and proper operation of all isolation and grounding devices (as applicable). |  |  |  |  |  |  |
|  | Check integrity of primary fuses (if applicable). |  |  |  |  |  |  |
|  | Check insulating liquid level (if applicable). |  |  |  |  |  |  |
|  | Voltage Transformer Electrical Check |  |  |  |  |  |  |
|  | Winding resistance test conducted and results are acceptable. |  |  |  |  |  |  |
|  | Insulation resistance test conducted and results are acceptable. |  |  |  |  |  |  |
|  | Polarity test conducted and results are acceptable. |  |  |  |  |  |  |
|  | Ratio test conducted and results are acceptable. |  |  |  |  |  |  |
|  | Burden test conducted and results are acceptable. |  |  |  |  |  |  |
|  | Trip Units Mechanical Check |  |  |  |  |  |  |
|  | Check for physical damage and defects. |  |  |  |  |  |  |
|  | Check for DC power supply. |  |  |  |  |  |  |
|  | Check for proper installation. |  |  |  |  |  |  |
|  | Rating plug verification. |  |  |  |  |  |  |
|  | Backlight verification. |  |  |  |  |  |  |
|  | Trip Units Electrical Check |  |  |  |  |  |  |
|  | Complete functional testing conducted. |  |  |  |  |  |  |
|  | Others |  |  |  |  |  |  |
|  | Switchgear is in good condition with no apparent damaged noticeable. |  |  |  |  |  |  |
|  | All indicators (current, voltage, pilot lights) are properly working. |  |  |  |  |  |  |
|  | Arc flash labels provided. |  |  |  |  |  |  |
|  | Safety mat provided all over the equipment perimeter. |  |  |  |  |  |  |
|  | Mechanical interlock for breaker assembly drawn-in/draw out tested and properly working. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |