| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
| CAUTION: SPACE HEATERS MAY BE ENERGIZED |  |  |  |  |  |  |  |
|  | Equipment is de-energized, safe and locked-out. |  |  |  |  |  |  |
|  | Nameplate parameters are in compliance with design documents. |  |  |  |  |  |  |
|  | Transformer is correctly tagged in accordance with design layout drawings. |  |  |  |  |  |  |
|  | Transformer installation, mountings and anchorage are in accordance with design drawings. |  |  |  |  |  |  |
|  | Grounding is in accordance with project specifications. |  |  |  |  |  |  |
|  | Shipping bracing materials, temporary shipping grounds/shorting steps are removed. |  |  |  |  |  |  |
|  | Oil storage tank levels are correct. |  |  |  |  |  |  |
|  | Oil filling tube is properly installed and sealed. The oil level indicator is reading correct level. |  |  |  |  |  |  |
|  | No oil leakage and/or seepage should be found on or around transformer. |  |  |  |  |  |  |
|  | Cooling system radiators are properly installed and free of physical damage. |  |  |  |  |  |  |
|  | Cooling system fans/pumps are correctly fitted and rotate freely. |  |  |  |  |  |  |
|  | All terminations are clean, undamaged and correctly aligned. |  |  |  |  |  |  |
|  | Porcelain bushings surface should be clean and free of cracks or scars. |  |  |  |  |  |  |
|  | All valves on oil lines are free to move in open and close directions. Flanges are well sealed. |  |  |  |  |  |  |
|  | Check that non-magnetic gland plates are installed when using single core cables. |  |  |  |  |  |  |
|  | All cables are identified, free of physical damage and adequately supported with bend radius in compliance with project specifications. |  |  |  |  |  |  |
|  | Check condition of all bushing joints and seals, and that that there is no fluid leak. |  |  |  |  |  |  |
|  | Pressure relief valve installation and wiring are correct. |  |  |  |  |  |  |
|  | Positive pressure is maintained on gas-blanketed transformers. |  |  |  |  |  |  |
|  | Safety gas channel and rupture disc are properly installed. |  |  |  |  |  |  |
|  | Inspect liquid temperature indicator and pressure-vacuum indicator for appropriate readings. |  |  |  |  |  |  |
|  | Tap changer mechanism is correctly fitted and locked in appropriate position. |  |  |  |  |  |  |
|  | All termination enclosures have correct gaskets and fixing bolts. |  |  |  |  |  |  |
|  | For breather type transformers check: - Position of the conservator valve - Silica gel condition/color |  |  |  |  |  |  |
|  | Produce punch list items for identified defects. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |