| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | Cabinet and General Installation |  |  |  |  |  |  |
|  | Permanent labels affixed, including for fans. |  |  |  |  |  |  |
|  | Air flow capacity and ESP indicated in the fan nameplate are same as the equipment schedule and approved document. |  |  |  |  |  |  |
|  | Motor rating in Hp (Kw) and insulation class conforms to the approved document. |  |  |  |  |  |  |
|  | Equipment tagging is in compliance to the as-build drawings. |  |  |  |  |  |  |
|  | Casing condition good: no dents, leaks, door gaskets installed. |  |  |  |  |  |  |
|  | Access doors close tightly - no leaks. |  |  |  |  |  |  |
|  | Flexible connection between duct and unit tight and in good condition. |  |  |  |  |  |  |
|  | Vibration isolation equipment installed and released from shipping locks. |  |  |  |  |  |  |
|  | Maintenance access acceptable for unit and components. |  |  |  |  |  |  |
|  | Internal sound attenuation installed (as applicable for arrayed fans). |  |  |  |  |  |  |
|  | Thermal insulation properly installed and according to specification. |  |  |  |  |  |  |
|  | Instrumentation installed according to specification (thermometers, pressure gages, flow meters, etc.). |  |  |  |  |  |  |
|  | Clean up of equipment completed per contract documents. |  |  |  |  |  |  |
|  | Filters installed and replacement type and efficiency permanently affixed to housing - construction filters removed. |  |  |  |  |  |  |
|  | Arrangement of internal accessories (filters, coil, humidifier, fans, etc.) as per approved document. |  |  |  |  |  |  |
|  | Transport blocks removed for centrifugal fans. |  |  |  |  |  |  |
|  | Valves, Piping, Accessories and Coils |  |  |  |  |  |  |
|  | Pipe fittings complete and pipes properly supported. |  |  |  |  |  |  |
|  | Pipes properly labeled. |  |  |  |  |  |  |
|  | Pipes properly insulated. |  |  |  |  |  |  |
|  | Strainers in place and clean. |  |  |  |  |  |  |
|  | Piping system properly flushed. |  |  |  |  |  |  |
|  | No leaking apparent around fittings. |  |  |  |  |  |  |
|  | All coils are clean and fins are in good condition. |  |  |  |  |  |  |
|  | All condensate drain pans clean and slope to drain, per spec. |  |  |  |  |  |  |
|  | Valves properly labeled. |  |  |  |  |  |  |
|  | Valves installed in proper direction (as applicable). |  |  |  |  |  |  |
|  | OSAT, MAT, SAT, RAT, chilled water supply sensors properly located and secure (related OSAT sensor shielded). |  |  |  |  |  |  |
|  | Sensors calibrated (see calibration section below). |  |  |  |  |  |  |
|  | P/T plugs and isolation valves installed per drawings. |  |  |  |  |  |  |
|  | Fans and Dampers |  |  |  |  |  |  |
|  | Supply fan and motor alignment correct. |  |  |  |  |  |  |
|  | Supply fan belt tension and condition good. |  |  |  |  |  |  |
|  | Supply fan protective shrouds for belts in place and secure. |  |  |  |  |  |  |
|  | Supply fan area clean. |  |  |  |  |  |  |
|  | Supply fan and motor properly lubricated. |  |  |  |  |  |  |
|  | Return/exhaust fan and motor aligned. |  |  |  |  |  |  |
|  | Return/exhaust fan belt tension and condition good. |  |  |  |  |  |  |
|  | Return/exhaust fan protective shrouds for belts in place and secure. |  |  |  |  |  |  |
|  | Return/exhaust fan area clean. |  |  |  |  |  |  |
|  | Return/exhaust fan and motor lube lines installed and lubed. |  |  |  |  |  |  |
|  | Filters clean and tight fitting. |  |  |  |  |  |  |
|  | Filter pressure differential measuring device installed and functional (magnahelic, inclined manometer, etc.). |  |  |  |  |  |  |
|  | Smoke and fire dampers installed properly per contract docs (proper location, access doors, appropriate ratings verified). |  |  |  |  |  |  |
|  | All dampers close tightly. |  |  |  |  |  |  |
|  | All damper linkages have minimum play. |  |  |  |  |  |  |
|  | Low limit freeze stat sensor located to deal with stratification and bypass. |  |  |  |  |  |  |
|  | Electrical and Controls |  |  |  |  |  |  |
|  | Pilot lights are functioning. |  |  |  |  |  |  |
|  | Power disconnects in place and labeled. |  |  |  |  |  |  |
|  | All electric connections tight. |  |  |  |  |  |  |
|  | Proper grounding installed for components and unit. |  |  |  |  |  |  |
|  | Safeties in place and operable. |  |  |  |  |  |  |
|  | Starter overload breakers installed and correct size. |  |  |  |  |  |  |
|  | Sensors calibrated. |  |  |  |  |  |  |
|  | Control system interlocks hooked up and functional. |  |  |  |  |  |  |
|  | Smoke detectors in place. |  |  |  |  |  |  |
|  | All control devices, pneumatic tubing and wiring complete. |  |  |  |  |  |  |
|  | Variable Frequency Drive |  |  |  |  |  |  |
|  | VFD powered (wired to controlled equipment). |  |  |  |  |  |  |
|  | VFD interlocked to control system. |  |  |  |  |  |  |
|  | Static pressure or other controlling sensor properly located and per drawings and calibrated. |  |  |  |  |  |  |
|  | Static pressure or other controlling sensor calibrated. |  |  |  |  |  |  |
|  | Drive location not subject to excessive temperatures. |  |  |  |  |  |  |
|  | Drive location not subject to excessive moisture or dirt. |  |  |  |  |  |  |
|  | Drive size matches motor size. |  |  |  |  |  |  |
|  | Internal setting designating the model is correct. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |