| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General Installation |  |  |  |  |  |  |
|  | General appearance good with no apparent damage. |  |  |  |  |  |  |
|  | Equipment nameplate nominal capacity conforms to the design and approved documents. |  |  |  |  |  |  |
|  | Cooler casing pressure rating conforms to the approved documents. |  |  |  |  |  |  |
|  | Equipment label is affixed and conforms to the as-build drawing tagging. |  |  |  |  |  |  |
|  | Proper vibration isolators installed and adjusted. |  |  |  |  |  |  |
|  | Seismic restrain in place. |  |  |  |  |  |  |
|  | Isolation valves and balancing valves installed. |  |  |  |  |  |  |
|  | Pipe fittings and accessories completed. |  |  |  |  |  |  |
|  | Pipes not supported on chillers. |  |  |  |  |  |  |
|  | Hydronic flushing completed and strainers cleaned. |  |  |  |  |  |  |
|  | No visible damage on condenser fins (for air cooled condenser). |  |  |  |  |  |  |
|  | Condenser water piping flushing completed (as applicable). |  |  |  |  |  |  |
|  | Evaporator air vent provided (for indoor chiller). |  |  |  |  |  |  |
|  | Refrigerant relief pipe extended to outside (for indoor chiller). |  |  |  |  |  |  |
|  | Accessories such as thermometers, pressure gauge and test plugs installed. |  |  |  |  |  |  |
|  | Flow meter (as required) and flow switch installed. |  |  |  |  |  |  |
|  | Equipment is properly charged and refrigerant in the tank is at the correct level. |  |  |  |  |  |  |
|  | No visible oil leakage. |  |  |  |  |  |  |
|  | Piping and flow direction labelled on piping. |  |  |  |  |  |  |
|  | Oil heater is properly functioning. |  |  |  |  |  |  |
|  | Oil filter clean. |  |  |  |  |  |  |
|  | Electrical and Controls |  |  |  |  |  |  |
|  | Power wiring installed properly. |  |  |  |  |  |  |
|  | All electrical components are grounded properly. |  |  |  |  |  |  |
|  | Control wiring, devices, and interlocks are hooked up. |  |  |  |  |  |  |
|  | Sensors calibrated (as per calibration certificate date or site method for calibration). |  |  |  |  |  |  |
|  | Electrical isolators are installed as per design. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |