| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | Cabinet and General Installation |  |  |  |  |  |  |
|  | Permanent equipment labels are fixed and matches the equipment tag in the as-build drawings. |  |  |  |  |  |  |
|  | Capacity indicated in the nameplate complies with the design requirements and as per approved documents. Capacity shall be confirmed as follows: - Cooling Capacity for Dx Type - Air Flowrate - ESP for Ducted System - Heating Capacity - Humidification Capacity |  |  |  |  |  |  |
|  | Motor rating in Hp (Kw) and motor insulation class conforms to the approved documents. |  |  |  |  |  |  |
|  | Casing in good condition with no visible damage. |  |  |  |  |  |  |
|  | Duct flexible connectors between duct and unit in good condition (as applicable). |  |  |  |  |  |  |
|  | Fan transport block removed (for centrifugal fans). |  |  |  |  |  |  |
|  | Vibration isolators installed and released from shipping locks. |  |  |  |  |  |  |
|  | Maintenance access acceptable for unit and components. |  |  |  |  |  |  |
|  | Thermal insulation properly installed and according to the Specification. |  |  |  |  |  |  |
|  | Instrumentation (thermometers, pressure gauges, etc.) installed according to the approved drawings. |  |  |  |  |  |  |
|  | Clean up of equipment completed as per contract requirement. |  |  |  |  |  |  |
|  | Air filters installed. |  |  |  |  |  |  |
|  | Valves, Piping, Accessories and Coil |  |  |  |  |  |  |
|  | Pipe fittings complete and pipes properly supported. |  |  |  |  |  |  |
|  | Pipes properly labeled. |  |  |  |  |  |  |
|  | Pipes properly insulated. |  |  |  |  |  |  |
|  | Strainers in place and clean. |  |  |  |  |  |  |
|  | Piping system properly flushed. |  |  |  |  |  |  |
|  | No leaking apparent around fittings. |  |  |  |  |  |  |
|  | All coils are clean and fins are in good condition. |  |  |  |  |  |  |
|  | All condensate drain pans clean and slope to drain, per spec. |  |  |  |  |  |  |
|  | Valves properly labeled. |  |  |  |  |  |  |
|  | Valves installed in proper direction (as applicable). |  |  |  |  |  |  |
|  | Sensors calibrated (see calibration section below). |  |  |  |  |  |  |
|  | P/T plugs and isolation valves installed per drawings. |  |  |  |  |  |  |
|  | Fan and Dampers |  |  |  |  |  |  |
|  | Supply fan and motor alignment correct. |  |  |  |  |  |  |
|  | Supply fan belt tension and in good condition. |  |  |  |  |  |  |
|  | Supply fan protective shrouds for belts in place and secure. |  |  |  |  |  |  |
|  | Supply fan area clean. |  |  |  |  |  |  |
|  | Supply fan and motor properly lubricated. |  |  |  |  |  |  |
|  | Filters clean and tight fitting. |  |  |  |  |  |  |
|  | Filter pressure differential measuring device installed and functional (magnahelic, inclined manometer, etc.) as applicable. |  |  |  |  |  |  |
|  | All dampers close tightly. |  |  |  |  |  |  |
|  | All damper linkages have minimum play. |  |  |  |  |  |  |
|  | Electrical and Controls |  |  |  |  |  |  |
|  | Pilot lights are functioning. |  |  |  |  |  |  |
|  | Power disconnects in place and labeled. |  |  |  |  |  |  |
|  | All electric connections tight. |  |  |  |  |  |  |
|  | Proper grounding installed for components and unit. |  |  |  |  |  |  |
|  | Safeties in place and operable. |  |  |  |  |  |  |
|  | Starter overload breakers installed and correct size. |  |  |  |  |  |  |
|  | Sensors calibrated. |  |  |  |  |  |  |
|  | BMS monitoring and control system interlocks hooked up and functional. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |