| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General Installation |  |  |  |  |  |  |
|  | Equipment labelling matches the equipment tagging as per the As-build. |  |  |  |  |  |  |
|  | Capacity of cooling tower matches the equipment schedule and approved documents. |  |  |  |  |  |  |
|  | Cooling Tower in good condition and no apparent damage noticed. |  |  |  |  |  |  |
|  | Fan belts properly installed and tensioned. |  |  |  |  |  |  |
|  | Fan shaft collars installed and tight. |  |  |  |  |  |  |
|  | Fan and motor lubricated. |  |  |  |  |  |  |
|  | Fan blade pitch adjusted (for propeller fans). |  |  |  |  |  |  |
|  | Tower basin access in place. |  |  |  |  |  |  |
|  | Tower basin sump strainers clean and sump filled. |  |  |  |  |  |  |
|  | Sump heater and other freeze protection in place (alarms, etc.) as applicable. |  |  |  |  |  |  |
|  | All appurtenances installed such as pressure and temperature gauges in the condenser water piping. |  |  |  |  |  |  |
|  | Spray water inlet strainer installed and spray nozzle clean. |  |  |  |  |  |  |
|  | Pipe fitting and accessories installation complete. |  |  |  |  |  |  |
|  | Make-up water piping installation complete including float valve or motorized valve and float switches/level sensors. |  |  |  |  |  |  |
|  | All piping are correctly labelled and valves are properly tagged. |  |  |  |  |  |  |
|  | Chemical treatment system or plan installed. |  |  |  |  |  |  |
|  | Water treatment report submitted. |  |  |  |  |  |  |
|  | Distribution header balanced. |  |  |  |  |  |  |
|  | Test plug installed. |  |  |  |  |  |  |
|  | Isolation and balancing valves installed as per drawing. |  |  |  |  |  |  |
|  | Gear box lubricated (as applicable for rotating water header with fix speed fan motor). |  |  |  |  |  |  |
|  | Electrical and Controls |  |  |  |  |  |  |
|  | Power to unit and disconnect installed. |  |  |  |  |  |  |
|  | All electrical components grounded. |  |  |  |  |  |  |
|  | Power available to the sump heater (as applicable). |  |  |  |  |  |  |
|  | Motor protection and safeties installed. |  |  |  |  |  |  |
|  | Sensors and field devices installed and calibrated. |  |  |  |  |  |  |
|  | Control system interlocks hooked up and functional. |  |  |  |  |  |  |
|  | Bypass valve and tower isolation valve spanning calibrated. |  |  |  |  |  |  |
|  | Motorized valves, dampers, and float switches functional. |  |  |  |  |  |  |
|  | Vibration alarm tested and functional. Short sensor wiring and verify shutdown of fan thru the BMS. |  |  |  |  |  |  |
|  | Test high and low water alarms and automatic closing/opening of make-up water. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |