| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General Check |  |  |  |  |  |  |
|  | Capacity of traction motors including all of elevator accessories conforms to the approved documentation. Lifting capacity shall be in accordance to Specification and equipment approved MAS (Material Approval Sheet) |  |  |  |  |  |  |
|  | Installation conforms to the requirement of ASME A.17 and accepted by the Client Representatives. |  |  |  |  |  |  |
|  | Lift Pit Check |  |  |  |  |  |  |
|  | Dimensions of the lift pit (length, width, depth) conforms to the plan and requirements of the elevator system. |  |  |  |  |  |  |
|  | Pit is clean and dry. |  |  |  |  |  |  |
|  | Car pit buffer provided and in good condition. Oil buffer shall be provided for lift car with traveling velocity more than 1.5 m/s. |  |  |  |  |  |  |
|  | Counter weight pit buffer provided and in good condition. Oil buffer shall be provided for lift car with traveling velocity more than 1.5 m/s. |  |  |  |  |  |  |
|  | Counterweight guard screen provided and weights are properly stacked and secured with isolators. |  |  |  |  |  |  |
|  | Lighting provided in the pit. |  |  |  |  |  |  |
|  | Pit switch provided to stop the elevator car manually from the pit. |  |  |  |  |  |  |
|  | Governor rope tension pulley has free movement. |  |  |  |  |  |  |
|  | Limit switches rollers have free movement. |  |  |  |  |  |  |
|  | Trailing cable properly terminated and in good condition. |  |  |  |  |  |  |
|  | Power outlet provided with GFCI or RCD. |  |  |  |  |  |  |
|  | Drain system or sump provide to remove accumulation of water. |  |  |  |  |  |  |
|  | Access ladder provide if depth is more than 915 mm. |  |  |  |  |  |  |
|  | Lift Car Check (Internal) |  |  |  |  |  |  |
|  | Capacity of the lift car is displayed or labelled inside the car. |  |  |  |  |  |  |
|  | Exhaust blower provided and in working order. |  |  |  |  |  |  |
|  | Alarm bell provided and operational. |  |  |  |  |  |  |
|  | Light point provided terminating in socket or holder. |  |  |  |  |  |  |
|  | Two-way communication handset provided. |  |  |  |  |  |  |
|  | Floor indication display provided. |  |  |  |  |  |  |
|  | Lift car internal condition is acceptable. Free from damage and scratches. |  |  |  |  |  |  |
|  | Car door condition is satisfactory and operable. |  |  |  |  |  |  |
|  | Clearance between car sill and landing sill is not more than 30mm. in each floor. |  |  |  |  |  |  |
|  | Lift Car Check (Top) |  |  |  |  |  |  |
|  | Maintenance switch provided to manually direct car (up or down). |  |  |  |  |  |  |
|  | Switch board provided for lighting and power sockets. |  |  |  |  |  |  |
|  | All metal part shall be earthed. |  |  |  |  |  |  |
|  | Hoist way lighting provided. |  |  |  |  |  |  |
|  | Retiring cam do not contact with the lever of gate locks. |  |  |  |  |  |  |
|  | Guide shoe liners (car and counter weight) in good condition and playing freely. |  |  |  |  |  |  |
|  | Trailing cable is in good condition with no visible damage. |  |  |  |  |  |  |
|  | Safety switch provided to manually stop car. |  |  |  |  |  |  |
|  | Car top structure is reinforced with no apparent denting when weight is applied. |  |  |  |  |  |  |
|  | Roller guides in good condition and properly lubricated. |  |  |  |  |  |  |
|  | Suspension ropes are adequately fastened. |  |  |  |  |  |  |
|  | Secured emergency manhole provided which can only be opened from the car top. |  |  |  |  |  |  |
|  | Machine Room Check |  |  |  |  |  |  |
|  | Machine room shall have door locking arrangement and should be kept locked. Double door arrangement shall be provided for access of equipment and should be self-closing/latching. |  |  |  |  |  |  |
|  | Machine room shall be provided with adequate cooling and ventilation. |  |  |  |  |  |  |
|  | Room shall be clean and tidy with sufficient lamination. |  |  |  |  |  |  |
|  | Break releasing device provided and in good condition. |  |  |  |  |  |  |
|  | Power outlet provided with GFCI or RCD. |  |  |  |  |  |  |
|  | Electrical system provided in compliance to ASME requirements such as phase reversal/failure protection, MCCB rating, earth leakage protection, earthing conductor size, etc. Electrical system is accepted including all required electrical testing. |  |  |  |  |  |  |
|  | All metal part shall be earthed. |  |  |  |  |  |  |
|  | Break shoe liners are in good condition. |  |  |  |  |  |  |
|  | Operation gear box in good working condition, lubricated with no visible oil spill. |  |  |  |  |  |  |
|  | Suspension ropes and traction sheaves in good condition. |  |  |  |  |  |  |
|  | Limit or directional switches in good working condition. |  |  |  |  |  |  |
|  | Speed governor in good condition and rotates freely. |  |  |  |  |  |  |
|  | ERD (Emergency rescue device) provided in the control panel as required by the contract. |  |  |  |  |  |  |
|  | Batteries are in good working condition. |  |  |  |  |  |  |
|  | Fire protection system provided such as pre-action sprinkler system and smoke detection interlocked to the electrical power supplies (shut trip feature) to turn-off prior to sprinkler discharge. |  |  |  |  |  |  |
|  | Tracking motor structural support and fixing is adequate and approved by the structural engineer. |  |  |  |  |  |  |
|  | Floor Landing Check |  |  |  |  |  |  |
|  | De-locking mechanism provided in each floor landings. |  |  |  |  |  |  |
|  | Landing doors are in good condition & sliding freely with no excessive force provided. |  |  |  |  |  |  |
|  | Hall button in good working condition. |  |  |  |  |  |  |
|  | Floor indicator in good working condition. |  |  |  |  |  |  |
|  | Fireman’s switch provided in ground floor and secondary recall floor. |  |  |  |  |  |  |
|  | Hoistway Check |  |  |  |  |  |  |
|  | Hoistway is clean and tidy. Dust paint provided as required. |  |  |  |  |  |  |
|  | Facia plates provided below each landing as required |  |  |  |  |  |  |
|  | Hoist way lighting provided and in good working condition. |  |  |  |  |  |  |
|  | All metal parts shall be earthed. |  |  |  |  |  |  |
|  | Traction cables in good condition, no visible entanglement, and excessive sagging. |  |  |  |  |  |  |
|  | Guide rail is structurally sound and properly installed including tie brackets, spreader brackets, bolting/fixing, and framings. |  |  |  |  |  |  |
|  | Sprinklers provided as per Code and statutory requirements. |  |  |  |  |  |  |
|  | Suitable some detectors provided at the top most location of the hoistway. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |