| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | The escalator/moving walk installed and inspected in accordance with ASTM A.17.1 Standards. |  |  |  |  |  |  |
|  | Assembly is in good condition with no apparent damages noticeable. |  |  |  |  |  |  |
|  | Capacity of traction motors including all of elevator accessories conforms to the approved documentation. Lifting capacity shall be in accordance to Specification and equipment approved MAS (Material Approval Sheet). |  |  |  |  |  |  |
|  | Escalators and moving walk material enclosure shall conform to non-combustible or limited-combustible definition by NFPA 101. |  |  |  |  |  |  |
|  | Adequate ventilation provided to the driving machine, control system, and truss enclosure spaces. |  |  |  |  |  |  |
|  | Construction requirements for the inclination and geometry (balustrades height and material used, handrails width and height, width and tread for moving walk, etc.) shall comply to the requirements of ASTM A.17.1 section 7.2 to 7.3. |  |  |  |  |  |  |
|  | Entrance and egress ends shall have comb plates and tread ways compliance to ASTM A.17.1 section 7.4. |  |  |  |  |  |  |
|  | Comb plate and comb step impact device or safety switch provided. |  |  |  |  |  |  |
|  | Entrance and exit zones free from any obstructions and obstacles. |  |  |  |  |  |  |
|  | No missing fixing screws for entrance and exit covers. |  |  |  |  |  |  |
|  | Deck barricade and anti-slide device provided for escalator. |  |  |  |  |  |  |
|  | Step and upthrust safety device and other safety devices (see functional test checklist for escalator and moving walk) provided for escalator and moving walk. |  |  |  |  |  |  |
|  | Is there adequate access and exit clearance from the end of the handrail? |  |  |  |  |  |  |
|  | Are the entry and exit points sufficiently illuminated? |  |  |  |  |  |  |
|  | Are the caution stickers provided and legible? |  |  |  |  |  |  |
|  | Is the escalator/moving walk stop switch provided, clearly labelled, and red in color? |  |  |  |  |  |  |
|  | Is the escalator/moving walk handrail in good condition? i.e. no sharp edges or other hazards where fingers can get caught or pinched. |  |  |  |  |  |  |
|  | Are all the combs in place? Max. 1 tooth missing in any one comb. Minimum comb teeth width 2.5mm. |  |  |  |  |  |  |
|  | Are the combs at least 6 mm deep meshing into step/belt guides? |  |  |  |  |  |  |
|  | Are there any signs of step misalignment – scraping marks on the sides of the guarding? |  |  |  |  |  |  |
|  | Step clearance between side of step and skirt guarding not exceeding 4mm gap. |  |  |  |  |  |  |
|  | Clearance between step edges (of consecutive steps) not exceeding 6 mm gap. |  |  |  |  |  |  |
|  | Does all the guarding have its locating screws/rivets in place? |  |  |  |  |  |  |
|  | Is the speed governor installed and in good condition? |  |  |  |  |  |  |
|  | Electrical power system installed according to NFPA 70 and ASMT A.17 requirements. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |