| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General Items |  |  |  |  |  |  |
|  | General Items |  |  |  |  |  |  |
|  | Equipment is de-energized, safe and locked-out. |  |  |  |  |  |  |
|  | Equipment is identified and tagged correctly in accordance with as-build drawings. |  |  |  |  |  |  |
|  | Nameplate parameters are in compliance with design documents. |  |  |  |  |  |  |
|  | Equipment has no visible signs of damage, including rust or corrosion. |  |  |  |  |  |  |
|  | Grounding is complete and in accordance with project specifications. |  |  |  |  |  |  |
|  | Pump foundations are complete and equipment is adequately anchored. |  |  |  |  |  |  |
|  | Grouting is complete. |  |  |  |  |  |  |
|  | Adequate space is available to permit equipment removal for maintenance with minimal piping, tray/conduit or other equipment dismantling. Lifting equipment is installed in accordance with design documents. |  |  |  |  |  |  |
|  | Auxiliary systems (i.e., lube oil, purge, quench, balance, cooling, seal, etc.) are properly installed with no visible signs of damage. |  |  |  |  |  |  |
|  | Lubrication grease (oil) is properly filled and lubrication tags or records are available. |  |  |  |  |  |  |
|  | Preservative compounds, greases, and oils are cleaned from equipment surfaces. Any desiccant is removed as required. |  |  |  |  |  |  |
|  | Forced lubrication systems are correctly piped and no leaks or openings are evident. |  |  |  |  |  |  |
|  | Coupling and guards are assembled or available. (Alignment records are required for turnover). |  |  |  |  |  |  |
|  | Visibly inspect for installation mechanical seals/packing. |  |  |  |  |  |  |
|  | Drains and vents are installed and adequately routed, if required. |  |  |  |  |  |  |
|  | Pump leak off is piped or channeled to convenient floor drain. |  |  |  |  |  |  |
|  | Strainers in suction piping are installed; and adequate means and space is available for cleaning. |  |  |  |  |  |  |
|  | Vibration instruments/probes are correctly mounted and undamaged. |  |  |  |  |  |  |
|  | Vibration panels are properly installed and internals are clean and free of debris or rust. Internal components are securely mounted and labeled in accordance with project specifications. |  |  |  |  |  |  |
|  | Components, including control/junction boxes, are clean and internal components are correctly installed and labeled. |  |  |  |  |  |  |
|  | Piping connections are correctly bolted with proper gasket materials (if visible). |  |  |  |  |  |  |
|  | All cabinets/control panels, junction boxes, etc. are properly sealed with door/covers closed and properly bolted. |  |  |  |  |  |  |
|  | Test manifold available with UL/FM flowmeter and gauge. Straight pipe lengths downstream and upstream of the flowmeter comply to the requirement of the flowmeter. |  |  |  |  |  |  |
|  | Sensing line completed and installed in-between the fire main line isolation and check valve with two (2) reverse check valve with 2.4 mm. hole spaced at 5ft. apart as specified by NFPA 20. |  |  |  |  |  |  |
|  | Main relief line and relief valve installed as required by the design (as applicable). |  |  |  |  |  |  |
|  | All appurtenances such as circulating relief valve, casing air release valve, liquid filled pressure gauges (compound type in the suction is required) installed. |  |  |  |  |  |  |
|  | Eccentric reducer provided in the suction of the pump. |  |  |  |  |  |  |
|  | Produce punch list items for identified defects. |  |  |  |  |  |  |
|  | For Electric Fire Pump |  |  |  |  |  |  |
|  | Circuit breaker for lock rotor overcurrent protection shall be 300% of the rated load current for induction motors. |  |  |  |  |  |  |
|  | Pilot lights are functioning. |  |  |  |  |  |  |
|  | All electrical connections inspected and approved. |  |  |  |  |  |  |
|  | Proper grounding installed for components and units. |  |  |  |  |  |  |
|  | For Diesel Fire Pump |  |  |  |  |  |  |
|  | Sand trap louver installed in room air intakes and room is properly ventilated. |  |  |  |  |  |  |
|  | Cooling water connections are available, inspected, and approved. |  |  |  |  |  |  |
|  | Fuel connections completed including fuel tanks. Installation of fuel system and containments conforms to standards. |  |  |  |  |  |  |
|  | Batteries and charger available and in good condition. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |