| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General Installation |  |  |  |  |  |  |
|  | General appearance good and no apparent damage. |  |  |  |  |  |  |
|  | Equipment label affixed and matches the equipment tagging in the as-build drawing. |  |  |  |  |  |  |
|  | Capacity indicated in the nameplate matches the capacity (KVA) based on service power rating (standby, prime power, or continuous power rating) and temperature derating in the design and approved documents. |  |  |  |  |  |  |
|  | Room space adequate for equipment and paralleling switchgear maintenance. |  |  |  |  |  |  |
|  | Required vibration isolation (inertia pad as required) and seismic restrain in place. |  |  |  |  |  |  |
|  | Exhaust piping completely installed including silencer and horizontal piping sloped properly. |  |  |  |  |  |  |
|  | Room has sufficient ventilation system and sand traps louvers. |  |  |  |  |  |  |
|  | Equipment completely installed inclusive of paralleling switchgear/switchboard, ATS, and NGR (Neutral Ground Resistors). All metering accessories (VT and CT), sensors, actuators, interlocks, etc. are completely installed and accepted. |  |  |  |  |  |  |
|  | All metallic parts are grounded. |  |  |  |  |  |  |
|  | All safety precaution and warnings are in place. |  |  |  |  |  |  |
|  | Equipment has passed the table shake testing (required in healthcare). Factory Certificates shall be provided. |  |  |  |  |  |  |
|  | Piping and Accessories |  |  |  |  |  |  |
|  | Fuel piping installed (transfer and supply/return) and tested inclusive of motorized valves and controls. |  |  |  |  |  |  |
|  | Fuel tanks (main and day tank) installed including appurtenances such as level float witches, level indicators, overflow, control valves, and controllers. |  |  |  |  |  |  |
|  | Isolation valves, fuel stop valves, and regulator installed. |  |  |  |  |  |  |
|  | Cooling piping and fittings including accessories installation completed. |  |  |  |  |  |  |
|  | Piping type and flow direction labelled on piping. |  |  |  |  |  |  |
|  | Pipes are painted, insulated, and cladded (as required). |  |  |  |  |  |  |
|  | Air vents and bleeds at high points of system available. |  |  |  |  |  |  |
|  | Exhaust Ducting |  |  |  |  |  |  |
|  | Exhaust air ducting provided with flexible connectors. |  |  |  |  |  |  |
|  | Louvers and effective exhaust opening comply to the requirements of the equipment. |  |  |  |  |  |  |
|  | Backdraft damper provided for multiple unit with common discharge plenum. |  |  |  |  |  |  |
|  | Electrical and Controls |  |  |  |  |  |  |
|  | Power to the unit and disconnect available. |  |  |  |  |  |  |
|  | Batteries are in good condition, filled with electrolyte and battery chargers properly working. |  |  |  |  |  |  |
|  | All electrical components grounded. |  |  |  |  |  |  |
|  | Sensors calibrated. |  |  |  |  |  |  |
|  | Control System interlocks hooked up and functional. |  |  |  |  |  |  |
|  | All control device and wiring complete for the ATS, Paralleling Switchgear/Switchboard and Genset Panel. |  |  |  |  |  |  |
|  | Engine and Alternator |  |  |  |  |  |  |
|  | Recirculating hydronic cooling system filled with water and coolant. |  |  |  |  |  |  |
|  | Radiator free from debris and excessive dust. |  |  |  |  |  |  |
|  | Engine heater working. |  |  |  |  |  |  |
|  | Starter kit in good working condition. |  |  |  |  |  |  |
|  | Radiator fan freely rotating with fan belt tension properly adjusted. |  |  |  |  |  |  |
|  | New oil filters in place. |  |  |  |  |  |  |
|  | Engine oil level is correct and engine oil type is as per manufacturer recommendation. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |