| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General Installation |  |  |  |  |  |  |
|  | Tanks are completely free from mud, sand, gravel, and other debris. |  |  |  |  |  |  |
|  | Pre-filter are installed to prevent large untreatable objects to enter the waste water tank. |  |  |  |  |  |  |
|  | The plant must be installed level with proper beddings or pads. |  |  |  |  |  |  |
|  | Plant that is installed partially or totally below grade, anchors shall be provide to avoid floatation. |  |  |  |  |  |  |
|  | Backfilling should be completed after tanks are set to avoid wall stress and ponding around the plant. |  |  |  |  |  |  |
|  | For metal tanks, cathodic protection must be connected prior to back filling. |  |  |  |  |  |  |
|  | Top of buried tanks are sufficiently above the finished grade to prevent surface water from entering the plant. |  |  |  |  |  |  |
|  | Perimeter fence are provided for safety and prevent vandalism. |  |  |  |  |  |  |
|  | The plant site should be covered with gravel. |  |  |  |  |  |  |
|  | A suitable access road to the plant must be provided for adequate maintenance. |  |  |  |  |  |  |
|  | Skimmers and sludge returns are equipped with proper valving. |  |  |  |  |  |  |
|  | Float in dosing chamber must be set at elevations noted on the approved plans to ensure proper dosing of the filter. |  |  |  |  |  |  |
|  | Block voids of filters must be filled with grout and walls sealed inside and outside with tar. |  |  |  |  |  |  |
|  | Filter sand is certified as acceptable for placement. |  |  |  |  |  |  |
|  | Chlorinator/dechlorinator units are installed correctly with the weir properly in place. |  |  |  |  |  |  |
|  | All tanks are properly marked with label and matching to the approved plans and as-builds. |  |  |  |  |  |  |
|  | Individual equipment (fans, pumps, mixer, aerators, etc.) are functional tested and accepted. Capacity of equipment verified in compliance to the approved documents. Equipment cycling control tested and functioning. |  |  |  |  |  |  |
|  | All water and air piping completed and tested including floats valves, switches, and meters. |  |  |  |  |  |  |
|  | All tanks are leak tested including connections. |  |  |  |  |  |  |
|  | High and low water level alarms provided, tested, and working properly. |  |  |  |  |  |  |
|  | All works for aeration tank, equalization tank, settling chamber, sludge holding tank, tertiary filters, chlorinator, and effluent dozing tank are completed and accepted. |  |  |  |  |  |  |
|  | Pipe, fittings and Appurtenances |  |  |  |  |  |  |
|  | Pipe fittings complete and pipes properly supported. |  |  |  |  |  |  |
|  | Pipes properly labeled. |  |  |  |  |  |  |
|  | Pipes properly insulated. |  |  |  |  |  |  |
|  | Strainers in place and clean. |  |  |  |  |  |  |
|  | Piping system properly flushed. |  |  |  |  |  |  |
|  | No leaking apparent around fittings. |  |  |  |  |  |  |
|  | All coils are clean and fins are in good condition. |  |  |  |  |  |  |
|  | All condensate drain pans clean and slope to drain, per spec. |  |  |  |  |  |  |
|  | Valves properly labeled. |  |  |  |  |  |  |
|  | Electrical and Controls Check |  |  |  |  |  |  |
|  | Pilot lights are functioning. |  |  |  |  |  |  |
|  | Power disconnects in place and labeled. |  |  |  |  |  |  |
|  | All electric connections tight. |  |  |  |  |  |  |
|  | Proper grounding installed for components and unit. |  |  |  |  |  |  |
|  | Safeties in place and operable. |  |  |  |  |  |  |
|  | Starter overload breakers installed and correct size. |  |  |  |  |  |  |
|  | Sensors calibrated. |  |  |  |  |  |  |
|  | Control system interlocks hooked up and functional. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |