| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General Installation |  |  |  |  |  |  |
|  | All equipment general appearance is good with no apparent damage. |  |  |  |  |  |  |
|  | Equipment nameplate (for pumps, fans, filters, etc.) nominal capacity conforms to the design and approved documents. |  |  |  |  |  |  |
|  | Corrosion resistant materials of construction are used for all equipment from the supply source to the membrane including piping, vessels, instruments and wetted parts of pumps. |  |  |  |  |  |  |
|  | All piping and equipment is compatible with designed pressure. |  |  |  |  |  |  |
|  | All piping and equipment is compatible with designed pH range (cleaning). |  |  |  |  |  |  |
|  | All piping and equipment is protected against galvanic corrosion. |  |  |  |  |  |  |
|  | Media filters are backwashed and rinsed. |  |  |  |  |  |  |
|  | New/clean cartridge filter is installed directly upstream of the high pressure pump. |  |  |  |  |  |  |
|  | Feed line, including RODI feed manifold, is purged and flushed, before pressure vessels are connected. |  |  |  |  |  |  |
|  | Chemical addition points are properly located. |  |  |  |  |  |  |
|  | Check/anti-siphon valves are properly installed in chemical addition lines. |  |  |  |  |  |  |
|  | Provisions exist for proper mixing of chemicals in the feed stream. |  |  |  |  |  |  |
|  | Dosage chemical tanks are filled with the right chemicals. |  |  |  |  |  |  |
|  | Provisions exist for preventing the RODI system from operating when the dosage pumps are shut down. |  |  |  |  |  |  |
|  | Provisions exist for preventing the dosage pumps from operating when the RODI system is shut down. |  |  |  |  |  |  |
|  | If chlorine is used, provisions exist to ensure complete chlorine removal prior to the membranes. |  |  |  |  |  |  |
|  | Planned instrumentation allows proper operation and monitoring of the pretreatment and RODI system. |  |  |  |  |  |  |
|  | Planned instrumentation is installed and operative. |  |  |  |  |  |  |
|  | Instrument calibration is verified. |  |  |  |  |  |  |
|  | Pressure relief protection is installed and correctly set. |  |  |  |  |  |  |
|  | Provisions exist for preventing the permeate pressure from exceeding the feed/concentrate pressure more than 5 psi (0.3 bar) at any time. |  |  |  |  |  |  |
|  | Interlocks, time delay relays and alarms are properly set. |  |  |  |  |  |  |
|  | Provisions exist for sampling permeate from individual modules. |  |  |  |  |  |  |
|  | Provisions exist for sampling raw water, feed, permeate and concentrate streams from each stage and the total plant permeate stream. |  |  |  |  |  |  |
|  | Pressure vessels are properly piped both for operation and cleaning mode. |  |  |  |  |  |  |
|  | Pressure vessels are secured to the rack or frame per manufacturer’s instructions. |  |  |  |  |  |  |
|  | Membranes are protected from temperature extremes (freezing, direct sunlight, heater exhaust, etc.). |  |  |  |  |  |  |
|  | Pumps are ready for operation: aligned, lubricated, proper rotation. |  |  |  |  |  |  |
|  | Fittings are tight. |  |  |  |  |  |  |
|  | Cleaning system is installed and operative. |  |  |  |  |  |  |
|  | Permeate line is open. |  |  |  |  |  |  |
|  | Permeate flow is directed to drain (In double-pass systems, provisions exist to flush first pass without permeate going through the second pass). |  |  |  |  |  |  |
|  | Reject flow control valve is in open position. |  |  |  |  |  |  |
|  | Feed flow valve is throttled and/or pump bypass is partly open to limit feed flow to less than 50% of operating feed flow. |  |  |  |  |  |  |
|  | All WTP components are properly installed such as Pre-treatments Units, RO skid, DI skid, and final filtration and UV Unit. |  |  |  |  |  |  |
|  | Pipe, fittings and Appurtenances |  |  |  |  |  |  |
|  | Pipe fittings complete and pipes properly supported. |  |  |  |  |  |  |
|  | Pipes properly labeled. |  |  |  |  |  |  |
|  | Pipes properly insulated. |  |  |  |  |  |  |
|  | Strainers in place and clean. |  |  |  |  |  |  |
|  | Piping system properly flushed. |  |  |  |  |  |  |
|  | No leaking apparent around fittings. |  |  |  |  |  |  |
|  | All coils are clean and fins are in good condition. |  |  |  |  |  |  |
|  | All condensate drain pans clean and slope to drain, per spec. |  |  |  |  |  |  |
|  | Valves properly labeled |  |  |  |  |  |  |
|  | Electrical and Controls Check |  |  |  |  |  |  |
|  | Pilot lights are functioning. |  |  |  |  |  |  |
|  | Power disconnects in place and labeled. |  |  |  |  |  |  |
|  | All electric connections tight. |  |  |  |  |  |  |
|  | Proper grounding installed for components and unit. |  |  |  |  |  |  |
|  | Safeties in place and operable. |  |  |  |  |  |  |
|  | Starter overload breakers installed and correct size. |  |  |  |  |  |  |
|  | Sensors calibrated. |  |  |  |  |  |  |
|  | Control system interlocks hooked up and functional. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |