| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
| 1 | Pressure Independent Control Valve to be use instead of conventional type. |  |  |  |  |  |  |
| 2 | Chiller evaporators and condensers are arranged in series-series configuration. |  |  |  |  |  |  |
| 3 | Demand for cooling exceeds 15,000 Tons as per ECRA Regulation ERD-TA-010 (District Cooling Regulatory Framework). Other requirements in the document shall also be applied prior to the implementation of DCS. |  |  |  |  |  |  |
| 4 | For projects located in low wet bulb temperature region, use of Free-cooling chillers with economizer specified. |  |  |  |  |  |  |
| 5 | As local regulation permits, Ammonia type chiller (either water cooled or air cooled) specified to reduce over-all power consumption especially in projects located in high wet-bulb temperature region where centrifugal chillers and cooling towers are very inefficient. |  |  |  |  |  |  |
| 6 | Thermal Storage Tank included in the design of DCS |  |  |  |  |  |  |
| 7 | Thermal Storage Tanks are design in parallel and stratified to optimize thermocline |  |  |  |  |  |  |
| 8 | Thermal Storage Tank type and location is considered based on the technology used. Location of project is also considered if there are potential for tank floatation in case of below grade installation. |  |  |  |  |  |  |
| 9 | DCS design provides operational sequence which states strategies for energy optimization as per Mashroat document EPM-KE0-GL-000004. |  |  |  |  |  |  |
| 10 | Delta T for chilled water supply and return maximized to reduce distribution pipe sizing and Thermal Storage Tank capacity. Delta T is in the range of 9° to 10°C, or higher. |  |  |  |  |  |  |
| 11 | DCS chiller controllers are manufacturer pre-programmed and pre-configure controllers intended for DCS application. |  |  |  |  |  |  |
| 12 | Fluid design velocity maximized to reduce distribution pipe size? |  |  |  |  |  |  |
| 13 | Standardization of building construction (for façade and roof), amount of fenestration, glazing characteristics, use of energy recovery, and building pressurization are implemented to limit variation in cooling load estimates. |  |  |  |  |  |  |
| 14 | The project development has high annual cooling load factor and high thermal load density for immediate Return of Investment (ROI). |  |  |  |  |  |  |
| 15 | When centrifugal chillers are used, sufficient supply of TSE (Treated Sewer Effluent) is available for Cooling Tower. TSE quality shall comply to ECRA Regulation ERD-TA-010 (District Cooling Regulatory Framework) |  |  |  |  |  |  |
| 16 | Specification requires the highest COP (or EER) and IPLV/NPLV for chillers |  |  |  |  |  |  |
| 17 | Specification requires the highest combined efficiency for pumps and motor |  |  |  |  |  |  |
| 18 | Chiller motor has high voltage power supply to reduce winding losses |  |  |  |  |  |  |
| 19 | Cooling tower and chiller energy balance study has been conducted to determine best delta T for condenser water to increase chiller-CT combined efficiency. |  |  |  |  |  |  |
| 20 | DCS uses primary chilled water distribution rather than primary-secondary to reduce capital investment and power consumption. |  |  |  |  |  |  |
| 21 | DCS plant is strategically located to reduce run of distribution piping thereby reducing friction head. |  |  |  |  |  |  |
| 22 | Substantial insulation thickness provided to reduce distribution piping heat gain and maximized cooling coil delta T. |  |  |  |  |  |  |
| 23 | Contraction/expansion joints and pipe anchors provided as per the Pipe Stress Analysis result to eliminate excessive stress in piping. |  |  |  |  |  |  |
| 24 | Sufficient depth for burial of distribution piping considered in the design. |  |  |  |  |  |  |
| 25 | Pro and cons on the type of Instrumentation and control considered between SCADA and BMS. Client to assess priority of importance to decide which system to be used. |  |  |  |  |  |  |
| 26 | DCS is designed for indirect connection to eliminate possible contamination of the system during each building commissioning and during O&M. HEx is designed for minimum approach (0.5 °C). |  |  |  |  |  |  |
| 27 | Use of atmospheric or vacuum deaerator considered in design for the closed loop. |  |  |  |  |  |  |
| 28 | Source of flushing water and discharge point of contaminated waste water considered during design to comply with COSHH. |  |  |  |  |  |  |
| 29 | Chemical dozing pot included for close distribution piping system flushing. Dozing pot connected between supply and return of the distribution pump. |  |  |  |  |  |  |
| 30 | Specification indicates required water chemistry (pH, conductivity, total hardness, alkalinity, chlorides, soluble iron, etc.) |  |  |  |  |  |  |
| 31 | Field device required accuracy and drift specified by the designer. |  |  |  |  |  |  |
| 32 | Closed evaporative cooling tower used for project located in dusty/sandy environment |  |  |  |  |  |  |
| 33 | Cooling towers was designed with self- cleaning basin. Side stream filtration provided in the condenser water piping for automatic removal of sand and dirt. |  |  |  |  |  |  |
| 34 | Cooling towers are located to have shading and not exposed to direct sunlight for minimizing biological growth. |  |  |  |  |  |  |
| 35 | Chilled water circuits, condenser water circuits, process water circuits (for closed cooling tower) provided with automatic chemical dosing system for water chemistry/quality maintenance. |  |  |  |  |  |  |
| 36 | Btu-meter interface with building chilled water system inclusive of PLC and fiber optic cable (including roughing-ins and field devices) ownership clearly identified in the drawings, specifications, and contract. Interface shall be closely coordinated between providers and end-users. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |