| PROJECT NAME: |  |  |  | DISCIPLINE: |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EQUIPMENT TYPE: |  | EQUIPMENT TAG: |  | EQUIPMENT LOCATION: |  |  |  |  |
| ELV System Integration |  |  |  |  |  |  |  |  |
| No. | QUESTIONS |  |  |  | ORIGINATOR |  |  |  |
|  |  |  |  |  | N/A | YES |  | NO |
| ELV (Extra Low Voltage) System Integration |  |  |  |  |  |  |  |  |
|  | Specification Requirements |  |  |  |  |  |  |  |
|  | A dedicated Specification is provided for ELV System Integration which includes sequence of operation of the following integrated systems, as applicable: |  |  |  |  |  |  |  |
|  | - Security and Access Control System to CCTV |  |  |  |  |  |  |  |
|  | - Security and Access Control System to Intrusion Detection System |  |  |  |  |  |  |  |
|  | - Security and Access Control System to Door Intercom System |  |  |  |  |  |  |  |
|  | - Public Address and Voice Alarm System to Digital Signage |  |  |  |  |  |  |  |
|  | - Public Address and Voice Alarm System to IP or Analogue TV |  |  |  |  |  |  |  |
|  | - Master clock Integration to BMS, FDAS, Voice and Data Infrastructure, Nurse Call System, Real Time Location System, Q-Matic, PAVA, and Parking Management and Assistance System. |  |  |  |  |  |  |  |
|  | - ADT (Admission, Discharge, and Transfer) to Voice and Data Infrastructure and Nurse Call System |  |  |  |  |  |  |  |
|  | - Nurse Call System Integration to Patient Room Lighting System, Security Panic Alarm, Enterprise Telephone System (or VoIP), and Wireless Network |  |  |  |  |  |  |  |
|  | - BMS (Building Management System) and EPMS (Electrical Power Management System) |  |  |  |  |  |  |  |
|  | - BMS Integration to Security and Access Control System |  |  |  |  |  |  |  |
|  | - BMS Integration to Lighting System |  |  |  |  |  |  |  |
|  | - BMS, EPMS, Security and Access Control, PAVA, and Q-Matic to Wireless Network |  |  |  |  |  |  |  |
|  | Routing and other communication level protocol requirements such as IP or Non-IP based (TCP/IP) are identified in the Specification for all ELV Systems. |  |  |  |  |  |  |  |
|  | Mains power supplies for controllers, interface modules, and devices are included (24v DC, 24v AC, or 220 v AC) in the Specification or POE (Power Over Ethernet) is required for ELV Systems. Requirements for essential power is indicated for POE and non-POE. |  |  |  |  |  |  |  |
|  | ELV System field devices power requirements matches the POE Switch Chassis power availability. Up to 15 watts for POE switch, up to 30 watts for POE plus, and up to 60 watts for Universal POE. |  |  |  |  |  |  |  |
|  | The architectural RCP reflects all ELV System field devices and third fix (Access Points, Speakers, exciters, CCTV camera, etc.) |  |  |  |  |  |  |  |
|  | Specification indicates preferred communication protocol for all ELV System. Communication protocol is truly open for inter-operability for all system level integration. |  |  |  |  |  |  |  |
|  | Designer must consider and coordinate aspects of system integration, such as Quality of Service (QoS), delay and packet loss management, delay variation, security, bandwidth, scalability, information storage, authorization level, and redundancy to ensure successful system integration |  |  |  |  |  |  |  |
|  | Design Site Survey was conducted for Wireless Network System to ensure proper signal strength coverage of each Access Points. Parameters used for the Site Survey has been discussed and accepted by the Client Representatives. |  |  |  |  |  |  |  |
|  | Specification clearly defines method of integration between systems, equipment, devices, and other items within the controller hierarchies. Integration method shall indicate either of the following method: - Electro-mechanical interlink thru relays and contactors. - Hardwire analogue integration by voltage (0-10 v, 0-5v, 2-10 volts), or current signal (4-20mA) - Hardwire digital integration - Hardwire software integration by Modbus, BACNet, LON, KNX, DALI, OPC, M-Bus, EnOcean, and other BAS protocol. - Fiber Optic software integration by Modbus, BACNet, LON, KNX, and other BAS protocol. - Communication cabling type. |  |  |  |  |  |  |  |
|  | ELV System Integration Diagram is developed and provided by the designer which includes methods of connection between systems, equipment, devices, and other items, inclusive of gateways as required. |  |  |  |  |  |  |  |
|  | Field devices (sensors, measuring devices, actuators, etc.) are NIST calibrated. Required criteria for the accuracy of field devices stated in the specification including device drift (during storage and during use) to identify re-calibration requirements. |  |  |  |  |  |  |  |
|  | Clear description of division of responsibilities between integrating parties. |  |  |  |  |  |  |  |
|  | A Commissioning Authority/ System Integrator was employed by the Client to provide comprehensive review and recommendation for all documents related to ELV Integration (e.g. ELV Integration Specification, BOD, OPR, etc.) to comply with the Client’s requirements, Codes, and Standards during the stages of design development. |  |  |  |  |  |  |  |
|  | Level controller control signal output matches field devices signal input and vice versa. |  |  |  |  |  |  |  |
|  | Testing and Commissioning requirements are defined in the Specification such as: |  |  |  |  |  |  |  |
|  | - Comprehensive methodology for Integrated Testing. |  |  |  |  |  |  |  |
|  | - Integration Testing Plan to include: |  |  |  |  |  |  |  |
|  | - Identification of procedure, limits, and process of inspection. |  |  |  |  |  |  |  |
|  | - Scope and list of systems, equipment, devices, and other items covered under the FLS Integration Program. |  |  |  |  |  |  |  |
|  | - Overview of the Integration Strategy. |  |  |  |  |  |  |  |
|  | - Milestone schedule. |  |  |  |  |  |  |  |
|  | - Integrating Agent Organizational Chart. |  |  |  |  |  |  |  |
|  | - Reporting procedure for progress, defects, and corrections |  |  |  |  |  |  |  |
|  | - Division of Responsibilities between Trade Contractors. |  |  |  |  |  |  |  |
|  | - Integration checklist and templates. |  |  |  |  |  |  |  |
|  | Training requirements for Maintenance Staff identified in the Specification (duration, programming, hands-on, external or local training, etc.) |  |  |  |  |  |  |  |
|  | Clear description of division of responsibilities and Scope of Work between integrating parties which includes provision of gateways as required. |  |  |  |  |  |  |  |
| 18 | Cyber Security needs to be addressed, assigned responsibility, and direction for codes to follow shall be included. |  |  |  |  |  |  |  |
| 19 | The degree of management of electrical protection settings, and the ability to change/edit either off-line (or on-line) with separate levels of password control should be addressed with regard to Electrical Power Management Systems. |  |  |  |  |  |  |  |
|  | Drawings, Tables and Diagrams |  |  |  |  |  |  |  |
| 20 | ELV Safety Integration Diagram is developed and provided by the designer which includes methods of connection between systems, equipment, devices, and other items, inclusive of gateways as required for inter-operability between different application level communication protocols. |  |  |  |  |  |  |  |
| 21 | The architectural RCP reflects all ELV System field devices/ third fix (smoke detectors, Access Points, strobes, speakers, camera, etc.). Architectural RCP is the only base layout/reference for almost all ELV field devices during design. |  |  |  |  |  |  |  |
| 22 | The architectural plan reflects all ELV System field devices/ third fix (manual pull stations, strobes, speakers, camera, data outlets, telephone outlets, etc.) installed on the wall. Architectural layout is the only base layout for ELV field devices installed on the wall during design and should show elevations of devices from finished floor. |  |  |  |  |  |  |  |
| 23 | The structured cabling lay-out complies to the total requirement of UTP cables for all ELV systems and matches the requirement of field devices as per architectural RCP and floor plan. |  |  |  |  |  |  |  |
| No. | Reviewer's Comments |  | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  |  | Checker's Name / Signature and Date: |  |  |  |  |  |