FIRE ALARM TESTING AND COMMISSIONING

Fire Detection Alarm System (FDAS) Test Package -Template

| Witnessed by : |  |
| --- | --- |
| Representing : |  |
| Signature : |  |
| Date : |  |
| System : | FIRE ALARM SYSTEM |
| Building : |  |
| Contract : |  |
| Client : |  |
| Consultant : |  |

| Remarks: |  |  |  |
| --- | --- | --- | --- |
| Date: | Engineer: |  | Sheet No. |
| ENGINEER’S REPORT SHEET |  |  |  |

| Client: |  | Contract No. : |  |
| --- | --- | --- | --- |
|  |  | MS No. : |  |
| Location: |  | System : |  |
|  |  | Unit No. : |  |
| Date: | Engineer: |  | Sheet No. |

| Client: |  | Contract No. : |  |
| --- | --- | --- | --- |
|  |  | MS No. : |  |
| Location: |  | System : |  |
|  |  | Unit No. : |  |
| INDEX |  |  |  |
| FIRE ALARM SYSTEM |  |  |  |
| 1 | Fire Alarm System – Pre-Commissioning Checklist |  |  |
| 2 | Battery Test / Calculations |  |  |
| 3 | MSFD Control Panels |  |  |
| 4 | Testing & Commissioning Reports |  |  |
| 5 | Commissioning Sheets |  |  |
| 6 | Sequence of Operation and Test Procedure |  |  |
| 7 | Loops and Description of Devices |  |  |

| Client: | Contract No. : |  |  |
| --- | --- | --- | --- |
|  | MS No. : |  |  |
| Location: | System : |  |  |
|  | Unit No. : |  |  |
| - FIRE ALARM SYSTEM - PRE-COMMISSIONING CHECK LIST |  |  |  |
| Addressable Fire Detection and Control |  |  |  |
| Project Name: |  |  |  |
| Location: |  |  |  |
| Initiating Device Circuit |  |  |  |
| No. of Initiating Device Loops: |  |  |  |
| No. of Control and Monitoring Loops: |  |  |  |
| Type of Cable: |  |  |  |
| Size of the Cable: |  |  |  |
| Style of Wiring: |  |  |  |
| Drawing Reference: |  |  |  |
| Loop 1 | Yes | No | Comments |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Grounding: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| Within Loop Capacity as per approved drawing: | Yes | No |  |
| Proper Identification per approved drawing: | Yes | No |  |
| Loop 2 | Yes | No | Comments |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Grounding: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| Within Loop Capacity as per approved drawing: | Yes | No |  |
| Proper Identification per approved drawing: | Yes | No |  |
| Loop 3 | Yes | No | Comments |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Grounding: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| Within Loop Capacity as per approved drawing: | Yes | No |  |
| Proper Identification per approved drawing: | Yes | No |  |
| Notification Circuits (NAC) /Speaker with strobes, Speakers |  |  |  |
| Number of Notification Circuits (NAC) |  |  |  |
| Style of Wiring: |  |  |  |
| Type of Cable: |  |  |  |
| Size of Cable: |  |  |  |
| Drawing Reference: |  |  |  |
| NAC Circuit 1 | Yes | No | Comments |
| Proper Identification as per approved drawing: | Yes | No |  |
| No. of Circuits as per approved drawing: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| NAC Circuit 2 | Yes | No | Comments |
| Proper Identification as per approved drawing: | Yes | No |  |
| No. of Circuits as per approved drawing: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| NAC Circuit 3 | Yes | No | Comments |
| Proper Identification as per approved drawing: | Yes | No |  |
| No. of Circuits as per approved drawing: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| NAC Circuit 4 | Yes | No | Comments |
| Proper Identification as per approved drawing: | Yes | No |  |
| No. of Circuits as per approved drawing: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| NAC Circuit 5 | Yes | No | Comments |
| Proper Identification as per approved drawing: | Yes | No |  |
| No. of Circuits as per approved drawing: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| NAC Circuit 6 | Yes | No | Comments |
| Proper Identification as per approved drawing: | Yes | No |  |
| No. of Circuits as per approved drawing: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| NAC Circuit 7 | Yes | No | Comments |
| Proper Identification as per approved drawing: | Yes | No |  |
| No. of Circuits as per approved drawing: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| Fireman’s Phone Circuits |  |  |  |
| No. of Phone Circuits: |  |  |  |
| Style of Cabling: |  |  |  |
| Type of Cable: |  |  |  |
| Size of Cable: |  |  |  |
| Drawing Reference: |  |  |  |
| Phone Circuits 1 | Yes | No | Comments |
| Proper Identification as per approved drawing: | Yes | No |  |
| No. of Circuits as per approved drawing: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| Phone Circuits 2 | Yes | No | Comments |
| Proper Identification as per approved drawing: | Yes | No |  |
| No. of Circuits as per approved drawing: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| Phone Circuits 3 | Yes | No | Comments |
| Proper Identification as per approved drawing: | Yes | No |  |
| No. of Circuits as per approved drawing: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| Network Wiring |  |  |  |
| Type of Cable: |  |  |  |
| Style of Wiring: |  |  |  |
| Size of Cable: |  |  |  |
| Drawing Reference: |  |  |  |
| Proper Identification as per approved drawing | Yes | No |  |
| Free from Grounding: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Free from Short Circuit: | Yes | No |  |
| Fire Alarm Control Panel |  |  |  |
| Type of Panel: |  |  |  |
| Device Capacity of the Panel: |  |  |  |
| Number of Panels: |  |  |  |
| Primary Power Requirement: |  |  |  |
| Type of Secondary Power: |  |  |  |
| Type: |  |  |  |
| Hours of Standby: |  |  |  |
| Type of Circuit Protection: |  |  |  |
| MDB Location: |  |  |  |
| Description | Yes | No | Comments |
| Correct Panel as per approval: | Yes | No |  |
| Correct Location as per approved drawing: | Yes | No |  |
| Correct Installation height as per approved drawing: | Yes | No |  |
| No Physical Damage to the Panel: | Yes | No |  |
| No Physical Damage to the Battery: | Yes | No |  |
| Free from Extraneous Voltage: | Yes | No |  |
| Proper Identification of Field Wiring: | Yes | No |  |
| Power Supply with proper Grounding: | Yes | No |  |
| Proper Cable Termination within the Panel: | Yes | No |  |
| Correct Performance of the Panel: | Yes | No |  |
| Alarm Initiating Devices |  |  |  |
| Smoke Detector | Yes | No | Comments |
| Type: |  |  |  |
| Sensitivity: |  |  |  |
| Number of detectors: |  |  |  |
| Correct type of detector as per approved drawing: | Yes | No |  |
| Correct physical address as per approved drawing: | Yes | No |  |
| Correct location as per approved drawing (Height/width, breadth) | Yes | No |  |
| Correct placement as per approved drawing: | Yes | No |  |
| No physical damage to Detectors: | Yes | No |  |
| Correct termination at the Detector terminals: | Yes | No |  |
| Correct functionality of the Devices: | Yes | No |  |
| Heat Detector | Yes | No | Comments |
| No. of Devices: |  |  |  |
| Type: |  |  |  |
| Temperature: |  |  |  |
| Correct Type of Detector as per approved drawing: | Yes | No |  |
| Correct Physical Address as per approved drawing: | Yes | No |  |
| Correct Location as per approved drawing (height/width, breadth) | Yes | No |  |
| Correct Placement as per approved drawing: | Yes | No |  |
| No Physical Damage to Detectors: | Yes | No |  |
| Correct Termination at the Detector Terminals: | Yes | No |  |
| Correct Functionality of the Devices: | Yes | No |  |
| Manual Call Point | Yes | No | Comments |
| No. of Normal Call Points: |  |  |  |
| No. of Weatherproof Call Points: |  |  |  |
| Type of Action: |  |  |  |
| Correct Type of Device as per approved drawing: | Yes | No |  |
| Correct Physical Address as per approved drawing: | Yes | No |  |
| Correct Location as per approved drawing: | Yes | No |  |
| Correct Location as per approved drawing (height/width, breadth) | Yes | No |  |
| Correct Placement as per approved drawing: | Yes | No |  |
| No Physical Damage to Detector: | Yes | No |  |
| Correct Termination at the Device Terminals: | Yes | No |  |
| Correct Functionality of the Devices: | Yes | No |  |
| Notification Peripherals | Yes | No | Comments |
| No. of Speakers: |  |  |  |
| No. of Sounders: |  |  |  |
| No. of Speaker with Strobes: |  |  |  |
| No. of Flashers: |  |  |  |
| Correct Quantity as per approved drawing: | Yes | No |  |
| Correct Location: | Yes | No |  |
| Correct Height from ground level as per approved drawing: | Yes | No |  |
| No Physical Damages during installation: | Yes | No |  |
| Proper Termination at each Terminal: | Yes | No |  |
| Sufficient dB Level: | Yes | No |  |
| Sufficient Candela Rating: | Yes | No |  |
| Monitoring Devices | Yes | No | Comments |
| No. of Monitoring Devices: |  |  |  |
| Correct Installation as per approved drawing: | Yes | No |  |
| No Physical Damages for the Devices: | Yes | No |  |
| Appropriate Monitor Points as per specification: | Yes | No |  |
| Devices Remain in Normal Condition: | Yes | No |  |
| Control Devices | Yes | No | Comments |
| No. of Control Devices: |  |  |  |
| Proper Installation as per approved drawing: | Yes | No |  |
| Proper Location as per approved drawing: | Yes | No |  |
| Correct Height from Ground Level: | Yes | No |  |
| No Physical Damages to the Panel: | Yes | No |  |
| Correct Functionality: | Yes | No |  |

SIGN OFF:

| On-behalf of | Name | Date | Signature |
| --- | --- | --- | --- |
| TRADE CONTRACTOR: |  |  |  |
| MAIN CONTRACTOR: |  |  |  |
| COMMISSIONING ENGINEER: |  |  |  |
| COMMISSIONING MANAGER: |  |  |  |
| CONSULTANT: |  |  |  |

| Project: |  |  |  |  |  |  |  |  |  | Panel Location: |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Package No. |  |  |  |  |  |  |  |  |  | Asset Code: |  |  |  | Sheet No. |  |  |
| Building: |  |  |  |  |  |  |  |  |  | Plant Ref: |  |  |  | Rev. |  |  |
| - Cable Testing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Loop/Zone |  | No. of Units | Insulation Resistance(MΩ) |  |  |  |  |  | Continuity of Cores, Earth, and Screen | Comments |  |  |  |  |  |  |
|  |  |  | Between Cores | Cores to Earth |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | L/N | L/E |  |  |  | N/E | (√) |  |  |  |  |  |  |  |
| Tested by: |  |  |  |  |  | Witnessed by: |  |  |  |  |  | Accepted by: |  |  |  |  |
| Date: |  |  |  |  |  | Date: |  |  |  |  |  | Date: |  |  |  |  |
| Test Instrument(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Client: |  |  |  |  | Contract No. : |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | MS No. : |  |  |
| Location: |  |  |  |  | System : |  |  |
|  |  |  |  |  | Unit No. : |  |  |
| - BATTERY AUTONOMY TEST |  |  |  |  |  |  |  |
|  | Description |  |  |  |  | Acceptable / Measured Data | Date |
| 1 | The fire alarm panel shall include stand by battery power to support the system in mains failure. |  |  |  |  |  |  |
|  | - 24 hours standby |  |  |  |  |  |  |
|  | - Disconnect the mains power and allow the batteries to discharge |  |  |  |  |  |  |
|  | - 30 minutes in alarm |  |  |  |  |  |  |
| Alarm Sequence Set and Battery Autonomy Test Commenced |  |  |  |  |  |  |  |
| Date: |  |  |  | Start Time: |  | Completion Time: |  |
| SUB: Battery Test / Date |  |  |  |  |  |  |  |
| S. No. |  | Test Time | Measured Voltage | Remarks |  |  |  |

SIGN OFF:

| On-behalf of | Name | Date | Signature |
| --- | --- | --- | --- |
| TRADE CONTRACTOR: |  |  |  |
| MAIN CONTRACTOR: |  |  |  |
| COMMISSIONING ENGINEER: |  |  |  |
| COMMISSIONING MANAGER: |  |  |  |
| CONSULTANT: |  |  |  |

| Client: |  |  | Contract No. : |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | MS No. : |  |  |
| Location: |  |  | System : |  |  |
|  |  |  | Unit No. : |  |  |
| - MSFD PANELS |  |  |  |  |  |
| Damper Panel Ref | Control Module Ref | MSFD Ref | Monitor Module Ref | Location | Remarks |

SIGN OFF:

| On-behalf of | Name | Date | Signature |
| --- | --- | --- | --- |
| TRADE CONTRACTOR: |  |  |  |
| MAIN CONTRACTOR: |  |  |  |
| COMMISSIONING ENGINEER: |  |  |  |
| COMMISSIONING MANAGER: |  |  |  |
| CONSULTANT: |  |  |  |

| Client: |  |  |  |  |  | Contract No. : |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | MS No. : |  |  |  |  |  |
| Location: |  |  |  |  |  | System : |  |  |  |  |  |
|  |  |  |  |  |  | Unit No. : |  |  |  |  |  |
| - TESTING & COMMISSIONING REPORTS |  |  |  |  |  |  |  |  |  |  |  |
| Details: |  |  |  |  |  |  |  |  |  |  |  |
| Fire Alarm Control Panel: |  |  |  |  |  |  |  |  |  |  |  |
| Manufacturer: |  |  |  |  |  |  |  |  |  |  |  |
| Model No: |  |  |  |  |  |  |  |  |  |  |  |
| Software Rev: |  |  |  |  |  |  |  |  |  |  |  |
| Building Name: |  |  |  |  |  |  |  |  |  |  |  |
| Panel Location: |  |  |  |  |  |  |  |  |  |  |  |
| Alarm Initiating Devices and Circuit Information |  |  |  |  |  |  |  |  |  |  |  |
| Device |  | Qty of Devices Installed |  |  | Circuit Style |  |  |  |  |  | Qty of Devices Tested |
| Manual Fire Alarm Call Points |  |  |  |  |  |  |  |  |  |  |  |
| Photo Detectors |  |  |  |  |  |  |  |  |  |  |  |
| Heat Detectors |  |  |  |  |  |  |  |  |  |  |  |
| Water Flow Switches |  |  |  |  |  |  |  |  |  |  |  |
| NOVAC |  |  |  |  |  |  |  |  |  |  |  |
| Foam System |  |  |  |  | - |  |  |  |  |  | - |
| Alarm Verification Feature |  |  |  |  | Disabled |  |  |  |  |  | Enabled |
| Speaker with Strobe |  |  |  |  |  |  |  |  |  |  |  |
| Speakers |  |  |  |  |  |  |  |  |  |  |  |
| Are Circuits Monitored for Integrity |  |  |  |  | Yes |  |  |  |  |  | No |
| Supervisory, Trouble & Monitoring Signal Initiating Devices and Circuit Information |  |  |  |  |  |  |  |  |  |  |  |
| Device |  | Qty of Devices Installed |  |  | Correct Text Label |  |  |  |  |  | Qty of Devices Tested |
| Sprinkler Zone Control Valve |  |  |  |  |  |  |  |  |  |  |  |
| Sprinkler Fire Hose Reel |  |  |  |  |  |  |  |  |  |  |  |
| MSFD |  |  |  |  |  |  |  |  |  |  |  |
| Generator Fuel Level |  |  |  |  |  |  |  |  |  |  |  |
| NOVAC System |  |  |  |  |  |  |  |  |  |  |  |
| Control Modules and Circuit Information |  |  |  |  |  |  |  |  |  |  |  |
| Device |  | Qty of Devices Installed |  |  | Correct Text Label |  |  |  |  |  | Qty of Devices Tested |
| Exhaust Fans |  |  |  |  |  |  |  |  |  |  |  |
| AHU |  |  |  |  |  |  |  |  |  |  |  |
| Roller Shutter |  |  |  |  |  |  |  |  |  |  |  |
| Access Controlled Doors |  |  |  |  |  |  |  |  |  |  |  |
| Damper Control |  |  |  |  |  |  |  |  |  |  |  |
| FCU |  |  |  |  |  |  |  |  |  |  |  |
| Door Holder |  |  |  |  |  |  |  |  |  |  |  |
| Lighting Control System |  |  |  |  |  |  |  |  |  |  |  |
| System Power Supply |  |  |  |  |  |  |  |  |  |  |  |
| - Primary (Main) |  |  |  |  |  |  |  |  |  |  |  |
| Nominal Voltage: |  |  |  |  |  |  |  |  |  |  |  |
| Over Current Protection Type: |  |  |  |  |  |  |  |  |  |  |  |
| Location: |  |  |  |  |  |  |  |  |  |  |  |
| - Secondary (Standby) |  |  |  |  |  |  |  |  |  |  |  |
| Storage Battery: |  |  |  |  |  |  |  |  |  |  |  |
| Type: |  |  |  |  |  |  |  |  |  |  |  |
| Check List: Prior to Any Testing |  |  |  |  |  |  |  |  |  |  |  |
| Description |  |  |  | Yes |  |  | No |  |  | Comments |  |
| Notifications are made to: |  |  |  |  |  |  |  |  |  |  |  |
| Building Occupants: |  |  |  |  |  |  |  |  |  |  |  |
| Building Management: |  |  |  |  |  |  |  |  |  |  |  |
| System Tests and Inspections |  |  |  |  |  |  |  |  |  |  |  |
| Type |  |  |  | Visual |  |  | Functional |  |  | Comments |  |
| Control Panel: |  |  |  |  |  |  |  |  |  |  |  |
| Interface Equipment: |  |  |  |  |  |  |  |  |  |  |  |
| Lamps/LEDs: |  |  |  |  |  |  |  |  |  |  |  |
| Primary Power Supply |  |  |  |  |  |  |  |  |  |  |  |
| Trouble Signals |  |  |  |  |  |  |  |  |  |  |  |
| Supervisory Signals |  |  |  |  |  |  |  |  |  |  |  |
| Ground Fault Monitoring |  |  |  |  |  |  |  |  |  |  |  |
| Secondary Power (Battery Condition) |  |  |  |  |  |  |  |  |  |  |  |
| Load Voltage |  |  |  |  |  |  |  |  |  |  |  |
| Charger Test |  |  |  |  |  |  |  |  |  |  |  |
| Notification Appliances |  |  |  |  |  |  |  |  |  |  |  |
| Audible |  |  |  |  |  |  |  |  |  |  |  |
| Visible |  |  |  |  |  |  |  |  |  |  |  |
| Speakers |  |  |  |  |  |  |  |  |  |  |  |
| Voice Clarity |  |  |  |  |  |  |  |  |  |  |  |
| Alarm Initiating, Supervisory and Control Device Tests & Inspections |  |  |  |  |  |  |  |  |  |  |  |
| Location/Address |  | Device Type |  |  | Receipt of Correct Text Label |  |  |  |  |  | Functional Test |
| Location & address of devices checked and confirmed |  | Devices have been checked for the correct type of device |  |  | Checked at the FAP |  |  |  |  |  | All devices have been activated and checked at the Panel |
| Passed |  | Passed |  |  | Passed |  |  |  |  |  | Passed |
| The device activation test sheets and printouts are attached with the document |  |  |  |  |  |  |  |  |  |  |  |
| The control and monitoring loops are attached with the document |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |
| When the network is completed, 1% of the devices already tested in the CUP are to be re-tested back to fire command center and the graphic package is to be checked and confirmed. |  |  |  |  |  |  |  |  |  |  |  |
| The CUP buildings cause and effect matrix will be tested standalone incorporating nodes 1 & 2. |  |  |  |  |  |  |  |  |  |  |  |
| Emergency Communications Equipment |  |  |  |  |  |  |  |  |  |  |  |
| Device |  |  | Visual |  | Functional |  |  |  | Comments |  |  |
| Phone Set |  |  |  |  |  |  |  |  |  |  |  |
| Phone Jacks |  |  |  |  |  |  |  |  |  |  |  |
| Off Hook Indicator |  |  |  |  |  |  |  |  |  |  |  |
| Amplifier(s) |  |  |  |  |  |  |  |  |  |  |  |
| Call in Signal |  |  |  |  |  |  |  |  |  |  |  |
| System Performance |  |  |  |  |  |  |  |  |  |  |  |
| Interface Equipment |  |  |  |  |  |  |  |  |  |  |  |
| Device |  |  | Visual |  | Device Operational |  |  |  | Simulated Operation |  |  |
| AHU |  |  |  |  |  |  |  |  |  |  |  |
| FCU |  |  |  |  |  |  |  |  |  |  |  |
| EXHAUST FAN |  |  |  |  |  |  |  |  |  |  |  |
| MSFD |  |  |  |  |  |  |  |  |  |  |  |
| ROLLER SHUTTER |  |  |  |  |  |  |  |  |  |  |  |
| ACCESS CONTROL |  |  |  |  |  |  |  |  |  |  |  |
| DOOR HOLDER |  |  |  |  |  |  |  |  |  |  |  |
| Supervisory Station Monitoring |  |  |  |  |  |  |  |  |  |  |  |
| Device |  |  | Visual |  | Functional |  |  |  | Comments |  |  |
| Alarm Signal |  |  |  |  |  |  |  |  |  |  |  |
| Alarm Restoration |  |  |  |  |  |  |  |  |  |  |  |
| Trouble Signal |  |  |  |  |  |  |  |  |  |  |  |
| Trouble Signal Restoration |  |  |  |  |  |  |  |  |  |  |  |
| Supervisory Signal |  |  |  |  |  |  |  |  |  |  |  |
| Notification of Testing Completion |  |  | Yes |  |  |  |  |  | No |  |  |
| Building Management |  |  |  |  |  |  |  |  |  |  |  |
| Building Occupants |  |  |  |  |  |  |  |  |  |  |  |
| THE FOLLOWING DID NOT OPERATE CORRECTLY |  |  |  |  |  |  |  |  |  |  |  |
| Interfacing works to complete - |  |  |  |  |  |  |  |  |  |  |  |
| System Restored to Normal Operation |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  |  |  |  | Time: |  |  |  |  |  |  |

SIGN OFF:

| On-behalf of | Name | Date | Signature |
| --- | --- | --- | --- |
| TRADE CONTRACTOR: |  |  |  |
| MAIN CONTRACTOR: |  |  |  |
| COMMISSIONING ENGINEER: |  |  |  |
| COMMISSIONING MANAGER: |  |  |  |
| CONSULTANT: |  |  |  |

| Client: |  |  | Contract No. : |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | MS No. : |  |  |
| Location: |  |  | System : |  |  |
|  |  |  | Unit No. : |  |  |
| - COMMISSIONING SHEETS |  |  |  |  |  |
| - Pre-Functional Testing (Installation) |  |  |  |  |  |
|  | PRE-REQUISITE |  |  | Yes/No | Remarks |
| 1 | Installation of containment: |  |  |  |  |
| 2 | Verify installation of cables per system requirement: |  |  | Yes |  |
| 3 | Ensure installation of devices per approved drawings: |  |  | Yes |  |
| 4 | Ensure installation of panels per approved drawings: |  |  | Yes |  |
| Comments: |  |  |  |  |  |
| On-behalf of |  | Name |  | Date | Signature |
| TRADE CONTRACTOR: |  |  |  |  |  |
| MAIN CONTRACTOR: |  |  |  |  |  |
| T&C AGENT: |  |  |  |  |  |
| T&C AGENT MANAGER: |  |  |  |  |  |
| CONSULTANT: |  |  |  |  |  |

| Client: |  |  | Contract No. : |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | MS No. : |  |  |
| Location: |  |  | System : |  |  |
|  |  |  | Unit No. : |  |  |
| - Startup / No Power |  |  |  |  |  |
|  | PRE-REQUISITE |  |  | Yes/No | Remarks |
| 1 | Ensure field wiring are free from ground/short circuit prior to terminate in the FA panel |  |  |  |  |
| 2 | Ensure proper identification of field wiring prior to terminate in the FA panel |  |  | Yes |  |
| 3 | Ensure no physical damage to devices / equipment. |  |  | Yes |  |
| 4 | Programing / Labeling |  |  | Yes |  |
| Comments: |  |  |  |  |  |
| On-behalf of |  | Name |  | Date | Signature |
| TRADE CONTRACTOR: |  |  |  |  |  |
| MAIN CONTRACTOR: |  |  |  |  |  |
| T&C AGENT: |  |  |  |  |  |
| T&C AGENT MANAGER: |  |  |  |  |  |
| CONSULTANT: |  |  |  |  |  |

| Client: |  |  | Contract No. : |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | MS No. : |  |  |  |
| Location: |  |  | System : |  |  |  |
|  |  |  | Unit No. : |  |  |  |
| - Pre-Functional Testing - Check Sheet |  |  |  |  |  |  |
|  | PRE-REQUISITE |  |  | Yes/No |  | Remarks |
| 1 | Switch on power |  |  |  |  |  |
| 2 | Connect batteries |  |  | Yes |  |  |
| 3 | Upload the program |  |  | Yes |  |  |
| 4 | Check panel configuration |  |  | Yes |  |  |
| Comments: |  |  |  |  |  |  |
| On-behalf of |  | Name |  |  | Date | Signature |
| TRADE CONTRACTOR: |  |  |  |  |  |  |
| MAIN CONTRACTOR: |  |  |  |  |  |  |
| T&C AGENT: |  |  |  |  |  |  |
| T&C AGENT MANAGER: |  |  |  |  |  |  |
| CONSULTANT: |  |  |  |  |  |  |

| Client: |  |  | Contract No. : |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | MS No. : |  |  |
| Location: |  |  | System : |  |  |
|  |  |  | Unit No. : |  |  |
| - Functional Performance Testing and Witness |  |  |  |  |  |
|  | PRE-REQUISITE |  |  | Yes/No | Remarks |
| 1 | Test the function of smoke detectors |  |  |  |  |
| 2 | Test the function of heat detectors |  |  | Yes |  |
| 3 | Test the function of Manual call points |  |  | Yes |  |
| 4 | Test the function of flow switch activation. |  |  | Yes |  |
| 5 | Test the function of NOVEC/VESDA system alarm |  |  | Yes |  |
| 6 | Test all the notification devices & very appropriate SPL/LUX levels etc. |  |  | Yes |  |
| 7 | Test the interface in line with approved C&E Matrix. |  |  | Yes |  |
| Comments: |  |  |  |  |  |
| On-behalf of |  | Name |  | Date | Signature |
| TRADE CONTRACTOR: |  |  |  |  |  |
| MAIN CONTRACTOR: |  |  |  |  |  |
| T&C AGENT: |  |  |  |  |  |
| T&C AGENT MANAGER: |  |  |  |  |  |
| CONSULTANT: |  |  |  |  |  |

| Client: |  |  | Contract No. : |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | MS No. : |  |  |
| Location: |  |  | System : |  |  |
|  |  |  | Unit No. : |  |  |
| - Integration Testing |  |  |  |  |  |
|  | PRE-REQUISITE |  |  | Yes/No | Remarks |
| 1 | Connect Network Cables |  |  |  |  |
| 2 | Upload Network Programs |  |  |  |  |
| 3 | Test N/W Points in the Area FACPs |  |  |  |  |
| 4 | Test NDUs |  |  |  |  |
| 5 | Test Graphics |  |  |  |  |
| Comments: |  |  |  |  |  |
| On-behalf of |  | Name |  | Date | Signature |
| TRADE CONTRACTOR: |  |  |  |  |  |
| MAIN CONTRACTOR: |  |  |  |  |  |
| T&C AGENT: |  |  |  |  |  |
| T&C AGENT MANAGER: |  |  |  |  |  |
| CONSULTANT: |  |  |  |  |  |

| Client: |  |  | Contract No. : |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | MS No. : |  |  |  |  |
| Location: |  |  | System : |  |  |  |  |
|  |  |  | Unit No. : |  |  |  |  |
| - Handover |  |  |  |  |  |  |  |  |
|  | PRE-REQUISITE |  |  | Yes/No |  |  | Remarks |  |
| 1 | Training |  |  |  |  |  |  |  |
| 2 | Documentation |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |
| On-behalf of |  | Name |  |  | Date | Signature |  |  |
| TRADE CONTRACTOR: |  |  |  |  |  |  |  |  |
| MAIN CONTRACTOR: |  |  |  |  |  |  |  |  |
| T&C AGENT: |  |  |  |  |  |  |  |  |
| T&C AGENT MANAGER: |  |  |  |  |  |  |  |  |
| CONSULTANT: |  |  |  |  |  |  |  |  |

| Client: |  |  | Contract No. : |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | MS No. : |  |  |  |  |
| Location: |  |  | System : |  |  |  |  |
|  |  |  | Unit No. : |  |  |  |  |
| 6. SEQUENCE OF OPERATION AND TEST PROCEDURES |  |  |  |  |  |  |  |  |
| Pre-Start Checks / Pre-Commissioning (PFT) |  |  |  |  |  |  |  |  |
| Ensure the installation of the system confirms to the standards recommended by local Civil Defence Authority and NFPA. |  |  |  |  |  |  |  |  |
| - Pre-Start Checks / Pre-Commissioning (PFT) |  |  |  |  | Function Test |  | Remarks |  |
| - All fire alarm panels shall be in accessible locations |  |  |  |  |  |  |  |  |
| - Dedicated power supply for FACP |  |  |  |  |  |  |  |  |
| - All voice evacuation circuits shall be class A and outgoing and incoming cables shall follow different path physically. |  |  |  |  |  |  |  |  |
| - Recommended to have 100% detection and access for periodical maintenance of devices. |  |  |  |  |  |  |  |  |
| - Maximum distance between Manual call stations shall not be more than 20m. |  |  |  |  |  |  |  |  |
| - Standard installation heights of Manual call stations, Fireman’s phone jack, and Notification peripherals shall be 1220mm, 1520mm and 2300mm from FFL Respectively. |  |  |  |  |  |  |  |  |
| - Check if the field wires properly identified prior to making connection. |  |  |  |  |  |  |  |  |
| Identify the field wiring and make sure there is no extraneous voltages, grounding, and short circuit in appropriate circuits. |  |  |  |  |  |  |  |  |
| - Select a circuit, check the voltage using multi meter for extraneous voltage. Check all circuits prior to connecting to the panel. |  |  |  |  |  |  |  |  |
| - Select a circuit to check the resistance of the cable using a multi meter. The reading shall be No greater than 36ohms. Complete continuity checks for all circuits prior to connecting to the panel. |  |  |  |  |  |  |  |  |
| When all devices and modules installed, a measuring instrument to be used to validate the integrity of a loop and all connected devices checking for: |  |  |  |  |  |  |  |  |
| - Heads missing: The sensor head not installed on the base. Test report can be used to prove the sensor was not installed during installation |  |  |  |  |  |  |  |  |
| - Invalid Address: An invalid address is 0,251 to 255. IDNET supports address 1 to 250 |  |  |  |  |  |  |  |  |
| - Duplicated Address: More than one device is set to the same address. Use the LED ON feature to find the duplicate devices. |  |  |  |  |  |  |  |  |
| - Out of range: The sensor analog value is out of acceptable range, most likely a dirty sensor. Replace or clean the sensor. |  |  |  |  |  |  |  |  |
| - Unknown device: The measuring instrument does not recognize the device at this address. Run a duplicate device test / Bad device. |  |  |  |  |  |  |  |  |
| Through pre-testing, determine conformance of the system to the requirements of the approved drawings and specification |  |  |  |  |  |  |  |  |
| - Upon connecting all field circuit to the FACP, initiate some Fire Alarm devices randomly and check the performance in line with approved drawings prior to final testing |  |  |  |  |  |  |  |  |
| Correct deficiencies if observed on pre-testing, rapid malfunctioning or damaged items shall be re-tested until satisfactory performance and conditions are achieved. |  |  |  |  |  |  |  |  |
| - Commissioning / Test Procedures (FPT) |  |  |  |  | Function Test |  | Remarks |  |
| System provider shall commission the system and test the same in a standalone mode. |  |  |  |  |  |  |  |  |
| Following sequence shall be followed while conducting the tests |  |  |  |  |  |  |  |  |
| - Test and verify the functionality and Battery capacity of each Fire Alarm Control Panel (Node) prior to conduct any tests in the field devices. Battery Calculation sheet attached. |  |  |  |  |  |  |  |  |
| - Test 100 % field devices and appliances. All smoke detectors shall be tested using aerosol and heat detectors shall be tested with a heat generator (at least once) before it can be tested with other means such as magnetic test. |  |  |  |  |  |  |  |  |
| - FACP shall be tested to verify correct receipt of alarm, supervision, and fault signals (inputs) |  |  |  |  |  |  |  |  |
| - While 100% testing of devices, verify the receipt of alarm and correct text labeling on area FACP simultaneously. |  |  |  |  |  |  |  |  |
| Note: The same sequence shall be followed for all FACP’s. |  |  |  |  |  |  |  |  |
| - Initiating Devices |  |  |  |  |  |  |  |  |
| - Smoke Detectors: The Detector shall be tested to ensure smoke entry into the sensing chamber and an alarm response. Testing with smoke or listed aerosol approved by the manufacture shall be permitted as an acceptable test method. Detectors can be tested using magnetic rod. Place the magnetic rod near the TEST point on the detector base and hold for 10 seconds. |  |  |  |  |  |  |  |  |
| - Heat Detector: The detector shall be tested with a heat source per manufactures recommendation and alarm shall be verified. Detectors can be tested using magnetic rod. Place the magnetic rod near the TEST point on the detector base and hold it for 10 seconds. |  |  |  |  |  |  |  |  |
| - Manual Call Points - Alarms shall be verified by activating key operated manual call points |  |  |  |  |  |  |  |  |
| - Duct Detectors: Duct detectors shall be tested to ensure that the device will sample the air stream to activate. Spray aerosol into the duct at which sampling tubes are fixed or use the magnetic test point inside the detector enclosure. |  |  |  |  |  |  |  |  |
| - Zone Control Valve: Valve shall be operated, and supervisory signal receipt shall be verified to be within the first two revolutions of the hand wheel or per the manufacturer's published instructions. |  |  |  |  |  |  |  |  |
| - Sprinkler Flow Switch: Drain valve (Near each zone control valve) shall be opened to cause water flow and alarm receipt shall be verified. |  |  |  |  |  |  |  |  |
| Records: The above activities shall be recorded in each Area FACP as a historical log and can be retrieved as a print out from the relevant panel |  |  |  |  |  |  |  |  |
| - Create Field Fault (Randomly) |  |  |  |  |  |  |  |  |
| - Smoke detector missing |  |  |  |  |  |  |  |  |
| - Wrong device |  |  |  |  |  |  |  |  |
| - Bad answer |  |  |  |  |  |  |  |  |
| - No answer and verify the receipt of fault and correct text labeling |  |  |  |  |  |  |  |  |
| - AC Power Failure |  |  |  |  |  |  |  |  |
| - Negative to Ground |  |  |  |  |  |  |  |  |
| - Positive to Ground |  |  |  |  |  |  |  |  |
| - Battery Depleted |  |  |  |  |  |  |  |  |
| - Open Circuit |  |  |  |  |  |  |  |  |
| - Verify the receipt of System Faults in Area FACP. |  |  |  |  |  |  |  |  |
| Records: The above activities shall be recorded in each area FACP as a historical log and can be retrieved as a print out from the relevant panel |  |  |  |  |  |  |  |  |
| - Operation of Evacuation Signals and Auxiliary Functions (Outputs) |  |  |  |  |  |  |  |  |
| - While 100% testing of devices, verify the broadcast of evacuation and sounder signals from area FACP as per approved Cause & Effect Matrix. |  |  |  |  |  |  |  |  |
| - Fuses - The fuse ratings shall be verified. 230AC - 2A & 24VDC - 9A |  |  |  |  |  |  |  |  |
| - Lamps & LEDs - Press Lamp test button at each area FACP and verify all Lamps & LEDs are illuminated. |  |  |  |  |  |  |  |  |
| - Primary (Main) Power Supply - All secondary power shall be disconnected and tested under maximum load, including all alarm appliances requiring simultaneous operation. All secondary power shall be reconnected at the end of test. Ideal condition for maximum load is during the alarm condition. |  |  |  |  |  |  |  |  |
| Records: The above activities shall be recorded for each FACP as a historical log and can be retrieved as a print out from the relevant panel |  |  |  |  |  |  |  |  |
| - Secondary Power Supply |  |  |  |  |  |  |  |  |
| - All primary power supplies (Mains AC Power) shall be disconnected in area FACP and the occurrence of required trouble indication for loss of primary power shall be verified. |  |  |  |  |  |  |  |  |
| - Above condition shall prevail for 24hrs and at the 59th minute of the final hour, an alarm shall be generated for duration of 30 minutes to verify the ability of batteries to meet standby and alarm requirements at each area FACP. |  |  |  |  |  |  |  |  |
| Records: The above activities shall be recorded for each FACP as a historical log and can be retrieved as a print out from the relevant panel |  |  |  |  |  |  |  |  |
| - Testing and Verification of Fireman’s Phone |  |  |  |  |  |  |  |  |
| - Off Hook Indicator - Phone set shall be installed or shall be removed from hook and receipt of signal on Voice Command Center at Fire Command Center shall be verified (Network to be completed) |  |  |  |  |  |  |  |  |
| - Phone Jacks - Phone jack shall be visually inspected, communication path through jack shall be initiated and exact location shall be verified in the Fire Command Centre (Network to be completed) |  |  |  |  |  |  |  |  |
| - Select any fire zone and plug in handset into available jacks in the same zone. Then establish communication between Fire Command Centre. |  |  |  |  |  |  |  |  |
| - There are six simultaneous conversations possible at a given time. Repeat the testing sequence in the rest of the Zones and record the result in the testing and commissioning report. |  |  |  |  |  |  |  |  |
| - Programming and Testing Procedure resulting in modification made to the system |  |  |  |  |  |  |  |  |
| - When an initiating device, notification appliance or control relay is added, it shall be functionally tested. |  |  |  |  |  |  |  |  |
| - When an initiating device, notification appliance or control relay is deleted, another device, appliance or control relay on the circuit shall be operated. |  |  |  |  |  |  |  |  |
| - When changes are made to site- specific software, the following shall apply. |  |  |  |  |  |  |  |  |
| - All functions known to be affected by the changes or identified by a means that indicates changes shall be 100% tested. |  |  |  |  |  |  |  |  |
| - In addition, 10% of initiating devices that are not directly affected by the change, up to a maximum of 50 devices, also shall be tested and the correct system operation shall be verified. |  |  |  |  |  |  |  |  |
| - Changes to all control units connected or controlled by the system executive software shall require a 10 percent test of the system, including a test of at least one device on each input and output circuit to verify critical system functions such as notification appliances, control functions, and off-premises reporting |  |  |  |  |  |  |  |  |
| - Interface Procedure |  |  |  |  |  |  |  |  |
| S/N | Equipment / System | Description |  | Type of interface |  | Comments Pass/Fail |  |  |
| 1 | Staircase Pressurization Fan |  |  |  |  |  |  |  |
| 2 | Exhaust Fan |  |  |  |  |  |  |  |
| 3 | Car Park Supply & Extract Fan |  |  |  |  |  |  |  |
| 4 | Motorized Fire & Smoke Damper |  |  |  |  |  |  |  |
| 5 | Air Handling Unit |  |  |  |  |  |  |  |
| 6 | Smoke Louvres |  |  |  |  |  |  |  |
| 7 | FCU |  |  |  |  |  |  |  |
| 8 | Lifts |  |  |  |  |  |  |  |
| 9 | Escalators |  |  |  |  |  |  |  |
| 10 | Emergency / Lighting Control |  |  |  |  |  |  |  |
| 11 | Door Holders |  |  |  |  |  |  |  |
| 12 | Door Closer |  |  |  |  |  |  |  |
| 13 | Accordion Door |  |  |  |  |  |  |  |
| 14 | Security System |  |  |  |  |  |  |  |
| 15 | Fire Shutter |  |  |  |  |  |  |  |
| 16 | Smoke Guard System |  |  |  |  |  |  |  |
| 17 | Fire Pump Status |  |  |  |  |  |  |  |
| 18 | Fire Pump Status |  |  |  |  |  |  |  |
| 19 | VESDA |  |  |  |  |  |  |  |
| 20 | Kitchen Fire Suppression System |  |  |  |  |  |  |  |
| 21 | Gaseous Suppression System |  |  |  |  |  |  |  |
| 22 | Aqueous Foam Suppression System |  |  |  |  |  |  |  |
| 23 | PA System |  |  |  |  |  |  |  |
| 24 | Emergency Generators Status |  |  |  |  |  |  |  |
| 25 | Fuel Tank Level |  |  |  |  |  |  |  |
| 26 | Gate Barrier |  |  |  |  |  |  |  |
| 27 | Pre-Action System |  |  |  |  |  |  |  |
| 28 | EMCS |  |  |  |  |  |  |  |
| 29 | Auto dial facility |  |  |  |  |  |  |  |
| - Initiating Devices |  |  |  |  |  |  |  |  |
| S/N | Equipment | Alarm / Alert |  | Type of Signal |  | Comments Pass/Fail |  |  |
| 1 | Smoke Detector |  |  |  |  |  |  |  |
| 2 | Heat Detector |  |  |  |  |  |  |  |
| 3 | Manual Call Point |  |  |  |  |  |  |  |
| 4 | Duct Detector |  |  |  |  |  |  |  |
| 5 | Zone Control Valve |  |  |  |  |  |  |  |
| 6 | Sprinkler Flow Switch |  |  |  |  |  |  |  |
| - Documentation |  |  |  |  |  |  |  |  |
| - Pre-Commissioning Report |  |  |  |  |  |  |  |  |
| - Test & Commissioning Report |  |  |  |  |  |  |  |  |
| - Commissioning Logic Pack |  |  |  |  |  |  |  |  |
| - Cause and Effect Matrix |  |  |  |  |  |  |  |  |
| - Equipment and Instrumentation |  |  |  |  |  |  |  |  |
| - The following instruments will be used for commissioning. These will be selected as having the maximum field measuring accuracy and being the best suited to the function being measured, and will be applied as recommended by the manufacturer. - All instrumentation used for the testing of the Fire Alarm system must have up to date calibration certificates and be logged on the Instrument Log Sheet with a copy of the calibration certificate. |  |  |  |  |  |  |  |  |
| - Test Instruments |  |  |  |  |  |  |  |  |
| - Decibel Meter - Multimeter - Insulation Resistance Tester - Any other required testing instrument |  |  |  |  |  |  |  |  |
| - Demonstration Procedures |  |  |  |  |  |  |  |  |
| - After the system has been commissioned and all the relevant paperwork completed. It must be offered to the Commissioning Manager. He/she will organize a time and date with all relevant parties to witness the system. - After the system has been witnessed the witnessing team or individual will decide to sign off the system or not depending on the success of the witness. |  |  |  |  |  |  |  |  |

SIGN OFF:

| Name | Date | Signature |
| --- | --- | --- |

| 7. LOOPS AND DESCRIPTION OF DEVICES |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Device No. | Device Binary Address |  | Device Type | LOCATION OF DEVICE | Correct Installation | IR Testing | Device Tested | Device Status on FACP | REMARKS |