| PROJECT NAME: |  |  |  | DISCIPLINE: |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EQUIPMENT TYPE: |  | EQUIPMENT TAG: |  | EQUIPMENT LOCATION: |  |  |  |  |
| Fire and Life Safety Integration |  |  |  |  |  |  |  |  |
| No. | QUESTIONS |  |  |  | ORIGINATOR |  |  |  |
|  |  |  |  |  | N/A | YES |  | NO |
| Fire and Life Safety Integration |  |  |  |  |  |  |  |  |
|  | Preliminary Requirements |  |  |  |  |  |  |  |
|  | Design Site Survey (ekahau, cisco, air magnet, etc.) was conducted for Wireless Network System to ensure proper signal strength coverage of each Access Points. Parameters used for the Site Survey has been discussed and accepted by the Client Representatives. |  |  |  |  |  |  |  |
|  | Design consider PAVA amplifier capacity to handle simultaneous activation of speakers and increase in output during fire condition. |  |  |  |  |  |  |  |
|  | PAVA speaker and amplifier zoning matches the Fire Evacuation Strategy Zoning requirements. |  |  |  |  |  |  |  |
|  | Security and Access Control strategy in place to determine doors to remain close and doors to unlock during single and double knocking. |  |  |  |  |  |  |  |
|  | Evacuation strategy in place to determine use of elevator during evacuation and evacuation priority procedures in relation to public annunciation. |  |  |  |  |  |  |  |
|  | Zoned-smoke control system employed in the Fire and Life Safety Strategy as required by NFPA 101 for specific project application. |  |  |  |  |  |  |  |
|  | Elevator secondary recall level identified by the Architect and Fire/Life Safety Plan. |  |  |  |  |  |  |  |
|  | Dedicated 2-way emergency communication system is required (or Enterprise Phone System is recommended to use). |  |  |  |  |  |  |  |
| 9 | Mains power supplies for controllers, interface modules, and devices are included (24v DC, 24v AC, or 220 v AC) in the Specification or POE (Power Over Ethernet) is required for Low Current Systems, as applicable. Requirements for essential power shall also be indicated for POE and non-POE. POE shall comply to IEEE 802.3 |  |  |  |  |  |  |  |
| 10 | Low Current System (or ELV) field devices power requirements (as applicable) matches the POE Switch Chassis power availability (Up to 15 watts for POE switch, up to 30 watts for POE plus, and up to 60 watts for Universal POE in compliance to IEEE 802.3). |  |  |  |  |  |  |  |
| 11 | Cyber Security needs to be addressed, assigned responsibility, and direction to codes to follow included. |  |  |  |  |  |  |  |
|  | Specification Requirements |  |  |  |  |  |  |  |
| 12 | NFPA 72 Positive Alarm Sequence is applicable. |  |  |  |  |  |  |  |
| 13 | Controllers used for all Smoke Control Systems are UL 864 Certified/UUKL listed. |  |  |  |  |  |  |  |
| 14 | Specification states that Standalone and Integrated Testing of Low Current System related to Fire and Life Safety complies with NFPA 3 and 4 latest edition. |  |  |  |  |  |  |  |
| 15 | The OPR and Particular Specification is provided for Fire and Life Safety Integration which includes sequence of operation of following systems, equipment, devices, and items be connected to the Fire Alarm Control Panel (FACP), as applicable: |  |  |  |  |  |  |  |
|  | - Low Current System (or ELV) such as: |  |  |  |  |  |  |  |
|  | - Building Management System |  |  |  |  |  |  |  |
|  | - Security and Access Control to include Intrusion Detection |  |  |  |  |  |  |  |
|  | - Public Address and Voice Alarm System |  |  |  |  |  |  |  |
|  | - Close Circuit Television Camera Tracking System |  |  |  |  |  |  |  |
|  | - Audio-Visual System |  |  |  |  |  |  |  |
|  | - Data Infrastructure and Wireless Network System |  |  |  |  |  |  |  |
|  | - Mechanical Life- Safety Systems such as: |  |  |  |  |  |  |  |
|  | - Staircase Pressurization System |  |  |  |  |  |  |  |
|  | - Lift Lobby or Lift Shaft Pressurization System |  |  |  |  |  |  |  |
|  | - Atrium Smoke Extraction System |  |  |  |  |  |  |  |
|  | - Car Parking Smoke Management System |  |  |  |  |  |  |  |
|  | - Elevator primary and secondary recall |  |  |  |  |  |  |  |
|  | - Sprinkler Flow Switch and Valve Supervisory Switch |  |  |  |  |  |  |  |
|  | - Door Hold-open electro-magnetic hardware for smoke partitions |  |  |  |  |  |  |  |
|  | - Main Entrance doors for Atrium Smoke Exhaust make-up air |  |  |  |  |  |  |  |
|  | - Air ducting motorized dampers for smoke zones |  |  |  |  |  |  |  |
|  | - LPG solenoid valve closure during single or double knock detection |  |  |  |  |  |  |  |
|  | - Clean Agent Control Panel interlink for monitoring of fire/smoke detection status |  |  |  |  |  |  |  |
|  | - Pre-action System Control Panel interlink for monitoring of fire/smoke detection status |  |  |  |  |  |  |  |
|  | - Kitchen hood fire-suppression system interlink for Kitchen Exhaust Fan and Make-up AHU shutdown. |  |  |  |  |  |  |  |
|  | - Roll-up door interlink for security and access control. |  |  |  |  |  |  |  |
|  | - Drop curtains for smoke zone confinement in large and open areas (e.g. malls) |  |  |  |  |  |  |  |
|  | - Oxygen solenoid shut-off for healthcare |  |  |  |  |  |  |  |
|  | - Car parking exit and entry booms |  |  |  |  |  |  |  |
|  | - 2-way emergency communication system (PABX or VoIP Server interface) |  |  |  |  |  |  |  |
| 16 | Routing and other communication level protocol requirements such as IP or Non-IP based (e.g.TCP/IP) are identified in the Specification for all Low Current Systems integrated to the Fire Alarm System. |  |  |  |  |  |  |  |
| 17 | Specification indicates preferred communication protocol for all Low Current System. Communication protocol is truly open for inter-operability for all system level integration. |  |  |  |  |  |  |  |
| 18 | Designer must consider and coordinate aspects of system integration, such as Quality of Service (QoS), delay and packet loss management, delay variation, security, bandwidth, scalability, information storage, authorization level, and redundancy to ensure successful system integration |  |  |  |  |  |  |  |
| 19 | Specification clearly defines method of integration between systems, equipment, devices, and other items within the controllers. Integration method shall indicate either of the following method: - Electro-mechanical interlink thru relays and contactors. - Hardwire analogue integration by voltage (0-10 v, 0-5v, 2-10 volts), or current signal (4-20mA) - Hardwire digital integration - Hardwire software integration by BACNet, LON, Modbus, KNX, DALI, OPC, M-Bus, EnOcean, and other BAS protocol. - Fiber Optic software integration supported by BACNet, LON, Modbus, KNX, and other BAS protocol. - Type of communication cabling. |  |  |  |  |  |  |  |
| 20 | Level controller control signal output matches field devices signal input and vise-versa. |  |  |  |  |  |  |  |
| 21 | Fire Alarm Control Panel voice card is capable to handle requirement for public annunciation as per Fire Evacuation Plan. |  |  |  |  |  |  |  |
| 22 | Field devices (sensors, actuators, etc.) are NIST calibrated. Required criteria for the accuracy of field devices stated in the specification including device drift (during storage and during use) to identify re-calibration/replacement requirements. |  |  |  |  |  |  |  |
| 23 | A Commissioning Authority /Fire Commissioning Agent & Integrator was employed by the Client to provide comprehensive review and recommendation for all documents related to Fire and Life Safety System (e.g. FLS Integration Specification, BOD, OPR, etc.) to comply with the Client’s requirements, Codes, and Standards during the stages of design development. |  |  |  |  |  |  |  |
| 24 | Testing and Commissioning requirements are defined in the Specification such as: |  |  |  |  |  |  |  |
|  | - Comprehensive methodology for Integrated Testing. |  |  |  |  |  |  |  |
|  | - Integration Testing Plan to include: |  |  |  |  |  |  |  |
|  | - Identification of procedure, limits, and process of inspection. |  |  |  |  |  |  |  |
|  | - Scope and list of systems, equipment, devices, and other items covered under the FLS Integration Program. |  |  |  |  |  |  |  |
|  | - Overview of the Integration Strategy. |  |  |  |  |  |  |  |
|  | - Milestone schedule. |  |  |  |  |  |  |  |
|  | - FLS Integrator Third Party Agent Organizational Chart. |  |  |  |  |  |  |  |
|  | - Reporting procedure for progress, defects, and corrections |  |  |  |  |  |  |  |
|  | - Division of Responsibilities between Trade Contractors. |  |  |  |  |  |  |  |
|  | - Integration checklist and templates. |  |  |  |  |  |  |  |
| 25 | Training requirements for Maintenance Staff identified in the Specification (duration, programming, hands-on, external or local training, etc.) |  |  |  |  |  |  |  |
| 26 | Clear description of division of responsibilities and Scope of Work between integrating parties such as connections for secondary circuits/loops from interface modules. |  |  |  |  |  |  |  |
|  | Drawings, Tables and Diagrams |  |  |  |  |  |  |  |
| 27 | Fire and Life Safety Integration Diagram is developed and provided by the designer which includes methods of connection between systems, equipment, devices, and other items, inclusive of gateways as required. |  |  |  |  |  |  |  |
| 28 | The architectural RCP reflects all Low Current System (or ELV) field devices and third fix (smoke detectors, Access Points, strobes, speakers, camera, etc.). Architectural RCP is the only base layout/reference for almost all Low Current field devices during design. |  |  |  |  |  |  |  |
| 29 | The architectural plan reflects all Low Current System (or ELV) field devices and third fix (manual pull stations, strobes, speakers, camera, etc.) installed on the wall. Architectural layout is the only base layout for Low Current field devices installed on the wall during design. |  |  |  |  |  |  |  |
| 30 | Fire Detection and Alarm System Cause and Effect Matrix is prepared which includes time delay for the alarm notification and smoke control system activation as per NFPA 72. |  |  |  |  |  |  |  |
| 31 | Ensure documents and drawings meet the requirements specified in the OPR and applicable local regulations, codes, and standards. |  |  |  |  |  |  |  |
| No. | Reviewer's Comments |  | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  |  | Checker's Name / Signature and Date: |  |  |  |  |  |