| PROJECT NAME: |  |  | HVAC LAYOUT DWG NO. |  |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. | QUESTIONS |  | ORIGINATOR |  |  | CHECKER |  |  |
|  |  |  | N/A | YES | NO | N/A | YES | NO |
| 1 | Was the correct drawing template used (title block and borders)? |  |  |  |  |  |  |  |
| 2 | Was the latest background for the building/structure used? |  |  |  |  |  |  |  |
| 3 | Does the title block show the reason for issue/revision, and is the associated revision letter or number appropriate and consistent with Project Procedures? |  |  |  |  |  |  |  |
| 4 | Is the layout drawing number in accordance with Project Procedures? |  |  |  |  |  |  |  |
| 5 | Have all outstanding change papers (e.g., DCNs, FCDs, NCRs, etc.) been incorporated and noted as such in the title block? |  |  |  |  |  |  |  |
| 6 | Is there an Intellectual Property (IP)/Disclaimer Statement on the drawing? |  |  |  |  |  |  |  |
| 7 | Are the symbols for HVAC equipment, ducts, and any other specialty components in accordance with the Project's standard symbols and legends? |  |  |  |  |  |  |  |
| 8 | Are the tags assigned to equipment, ducts, dampers, specialty components, and floor/wall penetrations consistent with the associated riser diagram? |  |  |  |  |  |  |  |
| 9 | Are the equipment, duct, and damper sizes, materials/thicknesses, and configuration consistent with the latest version of the associated riser diagram? |  |  |  |  |  |  |  |
| 10 | Are there any markups on the master red-lined riser diagram (showing pending riser diagram changes) that need to be incorporated into the layout on this drawing? |  |  |  |  |  |  |  |
| 11 | Are there any changes that need to be marked on the master red-lined riser diagram to reflect the "as-built" configuration shown on this layout drawing? |  |  |  |  |  |  |  |
| 12 | Are duct sizes shown on main runs and branches (height x width for rectangular ducts or diameter for round ducts)? |  |  |  |  |  |  |  |
| 13 | Are duct materials and ratings (with correct thicknesses) shown on the drawing (or in the notes) and are they appropriate for the service? |  |  |  |  |  |  |  |
| 14 | Are duct elevations shown (e.g., from floor to: bottom of rectangular ducts or centerline of round ducts)? |  |  |  |  |  |  |  |
| 15 | Are duct horizontal dimensions shown if required (e.g., from centerline of building column or wall: to closest edge of rectangular ducts or centerline of round ducts)? |  |  |  |  |  |  |  |
| 16 | Are balancing dampers provided at each branch? |  |  |  |  |  |  |  |
| 17 | Are fire dampers included in duct penetrations through fire-rated walls if required? |  |  |  |  |  |  |  |
| 18 | Are backdraft or isolation dampers provided at fan/blower discharges if required? |  |  |  |  |  |  |  |
| 19 | Are ducts at equipment connections the correct sizes (to match information on supplier drawings) or are transition pieces included to mate up with equipment? |  |  |  |  |  |  |  |
| 20 | Are flexible connections or expansion joints shown where required for equipment connections? |  |  |  |  |  |  |  |
| 21 | Do calculations for duct sizing support the duct sizes shown on the drawing? |  |  |  |  |  |  |  |
| 22 | Do air velocities fall within industry guidelines? |  |  |  |  |  |  |  |
| 23 | Is the direction of flow indicated (if not obvious) for all duct runs? |  |  |  |  |  |  |  |
| 24 | Have Constructability requirements been considered? |  |  |  |  |  |  |  |
| 25 | Have Operability requirements been considered? |  |  |  |  |  |  |  |
| 26 | Has Accessibility for repair, maintenance, and inspection been considered? |  |  |  |  |  |  |  |
| 27 | Are duct and equipment access doors shown with appropriate space to open? |  |  |  |  |  |  |  |
| 28 | Is sufficient pull space provided for equipment or in-line components? |  |  |  |  |  |  |  |
| 29 | Are damper actuators located in accessible locations and are hand lever orientations shown? |  |  |  |  |  |  |  |
| 30 | Is space allotted for duct insulation if required (for either temperature or noise)? |  |  |  |  |  |  |  |
| 31 | Has an interference check been performed and have clashes been resolved? |  |  |  |  |  |  |  |
| 32 | Were all the match lines checked on this drawing and found to be correct? |  |  |  |  |  |  |  |
| 33 | Do the duct sizes and material/ratings on this drawing match other drawings at the interfaces (for all off-page connector match points)? |  |  |  |  |  |  |  |
| 34 | Is the duct routing as direct as possible to minimize the overall length of duct runs? |  |  |  |  |  |  |  |
| 35 | Is the duct routed to minimize interference ("cross-talk) between rooms? |  |  |  |  |  |  |  |
| 36 | Does the system design comply with applicable codes, standards, and regulatory requirements? |  |  |  |  |  |  |  |
| 37 | Does the system design comply with the applicable Project Mechanical Design Criteria, Project Scope Book, or any other Project Design Basis Documents? |  |  |  |  |  |  |  |
| 38 | Have sufficient section or elevation views been included on the drawing to clearly show the complete scope of work? |  |  |  |  |  |  |  |
| 39 | Are the notes appropriate and are they marked in applicable places on the drawing? |  |  |  |  |  |  |  |
| 40 | Are references made to applicable Standard Details where required to provide additional clarity? |  |  |  |  |  |  |  |
| 41 | Has appropriate interdisciplinary and intradepartmental coordination of the drawing been completed? |  |  |  |  |  |  |  |
| 42 | Has the Originator of the drawing resolved coordination comments and incorporated changes where required? |  |  |  |  |  |  |  |
| 43 | If required, has the drawing been stamped by a registered Professional Engineer? |  |  |  |  |  |  |  |
| 44 | On drawings "Issued for Construction" (Rev. 000 or higher), have areas of the drawing with incomplete designs or preliminary information been placed on hold? |  |  |  |  |  |  |  |
| 45 | If the drawing is being revised, are changes clearly shown (e.g., using clouds, revision triangles, or notes in the revision line of the title block)? |  |  |  |  |  |  |  |
| 46 | If the drawing is being revised, are all previous revision markings (clouds or triangles) removed? |  |  |  |  |  |  |  |
| No. | Reviewer's Comments (against each SLD) | Resolution |  |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |  |