| PROJECT NAME: |  |  | Mech. Plant Room Layout Drawing No. |  |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. | QUESTIONS |  | ORIGINATOR |  |  | CHECKER |  |  |
|  |  |  | N/A | YES | NO | N/A | YES | NO |
| 1 | Was the correct drawing template used (title block and borders)? |  |  |  |  |  |  |  |
| 2 | Was the latest background for the building/structure used? |  |  |  |  |  |  |  |
| 3 | Does the title block show the reason for issue/revision, and is the associated revision letter or number appropriate and consistent with Project Procedures? |  |  |  |  |  |  |  |
| 4 | Is the layout drawing number in accordance with Project Procedures? |  |  |  |  |  |  |  |
| 5 | Have all outstanding change papers (e.g., DCNs, FCDs, NCRs, etc.) been incorporated and noted as such in the title block? |  |  |  |  |  |  |  |
| 6 | Is there an Intellectual Property (IP)/Disclaimer Statement on the drawing? |  |  |  |  |  |  |  |
| 7 | Are equipment names and tag or mark numbers shown on the layout drawing? |  |  |  |  |  |  |  |
| 8 | Are building columns identified and dimensioned (with coordinates for "X" and "Y" axis directions)? |  |  |  |  |  |  |  |
| 9 | Are vertical dimensions shown on elevation sections (e.g., from floor to equipment connections/nozzles and top of equipment)? |  |  |  |  |  |  |  |
| 10 | Are horizontal dimensions shown (e.g., from centerline of building column or wall: to closest edge of equipment and any connections/nozzles)? |  |  |  |  |  |  |  |
| 11 | Is the equipment layout optimized for total installed cost (e.g., to allow for the most efficient pipe and duct runs while maintaining appropriate access to equipment)? |  |  |  |  |  |  |  |
| 12 | Are the control cabinets and electrical modules (e.g., motor control centers or switchgear) associated with the mechanical equipment located on the drawing? |  |  |  |  |  |  |  |
| 13 | If electrical/control equipment is present, is any pipe routed to avoid the space directly above this equipment and to meet any required separation criteria? |  |  |  |  |  |  |  |
| 14 | Are elevator shafts and hoist ways shown if required? |  |  |  |  |  |  |  |
| 15 | Is space shown (or reserved) for any pipe chases and duct shafts? |  |  |  |  |  |  |  |
| 16 | If permanent monorails are required to lift heavy equipment, are the rails located and are the lifting capacities identified? |  |  |  |  |  |  |  |
| 17 | If equipment removal hatches are required, is space reserved to access the hatch? |  |  |  |  |  |  |  |
| 18 | Are doorways shown for personnel and vehicle access (with direction of opening)? |  |  |  |  |  |  |  |
| 19 | Are aisles wide enough to meet local safety codes for personnel passageway? |  |  |  |  |  |  |  |
| 20 | Are aisles wide enough for a forklift (or other vehicle) to perform equipment maintenance or removal? |  |  |  |  |  |  |  |
| 21 | Are curbs or diked walls required to contain any hazardous materials? |  |  |  |  |  |  |  |
| 22 | For areas with hazardous materials, are Eye Wash Stations or Safety Showers located in easily accessible locations (to make a direct run using existing aisle)? |  |  |  |  |  |  |  |
| 23 | Is the floor material identified (e.g., grating, concrete, checkered plate, etc.)? |  |  |  |  |  |  |  |
| 24 | If sumps are required, are they shown with dimensions (length, width, and depth)? |  |  |  |  |  |  |  |
| 25 | Have floor drains been provided in convenient locations to allow for easy drainage of equipment if required for maintenance? |  |  |  |  |  |  |  |
| 26 | If there are any platforms or mezzanine levels, is the extent of the partial floor area identified in plan view (or in a section detail)? |  |  |  |  |  |  |  |
| 27 | If there are any platforms or mezzanine levels, is the difference in floor elevation identified (or shown in an elevation detail)? |  |  |  |  |  |  |  |
| 28 | Are stairways shown with up or down directions? |  |  |  |  |  |  |  |
| 29 | Have Constructability requirements been considered? |  |  |  |  |  |  |  |
| 30 | Have Operability requirements been considered? |  |  |  |  |  |  |  |
| 31 | Has Accessibility for repair, maintenance, and inspection been considered? |  |  |  |  |  |  |  |
| 32 | Are equipment access doors shown with appropriate space to open? |  |  |  |  |  |  |  |
| 33 | Is sufficient pull space and/or laydown space provided for equipment maintenance, repair, and/or replacement? |  |  |  |  |  |  |  |
| 34 | Has an interference check been performed and have clashes been resolved? |  |  |  |  |  |  |  |
| 35 | Are continuation layout drawing numbers provided at match lines and were they found to be correct? |  |  |  |  |  |  |  |
| 36 | Does the layout comply with the applicable Project Mechanical Design Criteria, Project Scope Book, or any other Project Design Basis Documents? |  |  |  |  |  |  |  |
| 37 | Have sufficient section or elevation views been included on the drawing to clearly show the complete scope of work? |  |  |  |  |  |  |  |
| 38 | Are the notes appropriate and are they marked in applicable places on the drawing? |  |  |  |  |  |  |  |
| 39 | Is there a Key Plan depicting other building/structure areas shown on the drawing? |  |  |  |  |  |  |  |
| 40 | Are references made to applicable General Arrangement or other drawings where required to provide additional clarity? |  |  |  |  |  |  |  |
| 41 | Has appropriate interdisciplinary and intradepartmental coordination of the drawing been completed? |  |  |  |  |  |  |  |
| 42 | Has the Originator of the drawing resolved coordination comments and incorporated changes where required? |  |  |  |  |  |  |  |
| 43 | If required, has the drawing been stamped by a registered Professional Engineer? |  |  |  |  |  |  |  |
| 44 | On drawings "Issued for Construction" (Rev. 000 or higher), have areas of the drawing with incomplete designs or preliminary information been placed on hold? |  |  |  |  |  |  |  |
| 45 | If the drawing is being revised, are changes clearly shown (e.g., using clouds, revision triangles, or notes in the revision line of the title block)? |  |  |  |  |  |  |  |
| 46 | If the drawing is being revised, are all previous revision markings (clouds or triangles) removed? |  |  |  |  |  |  |  |
| No. | Reviewer's Comments (against each SLD) | Resolution |  |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |  |