| Meter-level KPIs |  |  |
| --- | --- | --- |
| Checkpoint/Metric | EMIS View | What to look for |
| Annual Energy use with normalizing factors such as gross floor area and CDD | Annual Energy Use Intensity (EUI) in kWh/m2 or by fuel Energy Star portfolio manager benchmark score to gauge climate-normalized performance relative to peers | Rank portfolio and review outliers |
| Monthly Energy use with normalizing factors such as gross floor area and CDD | Monthly EUI in kWh/m2 or by fuel | Compare to previous month or previous year of the same month |
| Daily electricity KPI: (Total bldg. kWh/day)/(Avg. daily outdoor air temperature) | Min/max/average/current daily reading | Establish Facility benchmarks after commissioning |
| Daily gas KPI: (Total therms/day)/(Avg. daily outdoor air temperature) | Min/max/average/current daily reading | Establish Facility benchmarks after commissioning |
| Meter-level Analytics |  |  |
| Checkpoint | EMIS View | What to look for |
| Schedules | Use heat map and/or load profile graphs with filtering for weekday/weekend/holiday | Confirm that time-of-day schedules meet the current Facility requirements. Check weekends and holidays for scheduling improvement opportunities |
| Base load | Use heat map and/or load profile graphs with filtering for weekday/weekend/holiday | Compare to the peak load to assess the after-hour setback |
| Energy signature | Hourly Energy consumption vs. hourly outside air temperature (or daily Energy consumption vs. degree-days). Some EMIS automatically compare the Energy signature metrics to industry benchmarks | Weather-dependency of loads, balance point temperature at which heating or cooling starts, and base load. High heating Energy use in summer may be associated with simultaneous heating and cooling |
| Load shape | 24-hour demand plot, min/max/avg. by day type | Start time, stop time, weekend, and holiday scheduling |
| Energy anomaly | Flag when Energy use is outside the modeled prediction (see Appendix D for modeling instruction) | Energy use outside of a defined threshold of performance (+/- 10% for instance) |
| Meter data | Flag when meter has failed. A time series graph may be used to visually identify a gap | Large or repetitive (i.e. at regular intervals) gaps in Energy data |
| Energy Savings/M&V | The cumulative annual Energy savings, or % change in Energy use | Model statistics are within the thresholds set |
| System-level Key Performance Indicators |  |  |
| Checkpoint | EMIS View | What to look for (Establish Facility benchmarks after commissioning) |
| BMS Override Report | Building automation system override summary | Identify overrides that should not be in place. Overrides often point to larger system control or performance issues |
| BMS Alarm Report | List of recent alarms | Identify patterns in which systems are alarming. Potentially create Fault Detection and Diagnosis (FDD) rules to help troubleshoot alarms |
| Occupant Comfort Index (%) | % of operating hours spent within zone target temperature | Measure for each zone or collection of zones. Track average, minimum, and maximum values for each building |
| Cooling Plant Efficiency (kW/ton) | kilowatt (kW)/ton daily profile Daily Average (kW/ton)/ton kW of entire plant preferred, but pump metering is not always available | Will vary based on load. Review kW/ton vs. ton plots over time to identify performance drift |
| Heating Plant Efficiency (%) | - kW (out)/kW (in) - Review daily profile | Will vary based on load. Review efficiency vs. load plots over time to identify performance drift |
| Fan System Efficiency (%) | kW of supply/return/exhaust fans per cubic feet per minute (cfm) of airflow | Will vary based on load. Look for variance between air handlers or performance drift |
| Chilled water delta | Daily average difference in chilled water supply and return temperatures | If there is an insufficient temperature difference, investigate over-pumping or other issues |

Table 1: Monitoring Action Plan – Checkpoints and Metrics

| Fault Detection and Diagnosis |  |
| --- | --- |
| Faults | FDD Tool Analysis |
| General Faults |  |
| Schedules (AHUs), terminal units, chillers, boilers, pumps, cooling towers, plug and process loads, and garage exhaust fans) | Check if equipment is operating out of hours. |
| Manual override (AHUs, terminal units, chillers, boilers, pumps, and cooling towers) | Identify overrides that should not be in place. |
| Controllers (actuators/valves/speed drives) | - Compare controller output set-points to the actual condition to find failed devices. - Determine the stability of controllers. |
| Dampers (AHUs, terminal units) | Identify if a damper is stuck open, closed, or at a fixed position, or leaking (i.e. compare mixed air temperature to return air temperature with outdoor air damper closed). |
| Cooling/heating/precooling/preheating/ reheating valve and coils | - Identify if a valve is stuck or leaking. - Identify a fouled or blocked coil (i.e. a temperature difference exists across a coil when a valve is shut or not achieving a desired temperature drop across a coil when a valve is open). |
| Air Handler Faults |  |
| Economizer operation/use | - Detect if the RTU or AHU is not economizing when it should. - Detect if the RTU/AHU is economizing when it should not (i.e. calculate relevant theoretical outdoor air ratio with outdoor air temperature, return air temperature, and mix air temperature). - Detect if the economizer lockout set point is too high or low. |
| Ventilation | Ensure that the ventilation rate is adequate. Detects if the RTU/AHU is bringing in too much outside air when not in economizer mode. |
| Simultaneous heating and cooling | Detect if unnecessary heating, economizer cooling, and/or mechanical cooling happen at the same time. |
| Discharge air temperature reset | Identify if the discharge air temperature set point is a fixed value or does not vary through the reset range. Confirm that the point is not frequently pegged to an upper or lower limit. |
| Duct static pressure reset | Identify if the duct static pressure set point is a fixed value or does not vary through the range. Confirm that the point is not frequently pegged to an upper or lower limit. |
| Sensors | - Critical sensors: Outdoor air, discharge air, return air, and mixed air temperature; wet bulb temperature or relative humidity; pressure; airflow rates. - Detect flatlining, bias, drift, or failure in sensor or if the sensor is outside of a feasible range. |
| Dirty Filter | Determine if the air filter needs replacement (i.e. filter pressure drop outside specified range). |
| Variable Air Volume (VAV) Box Faults |  |
| Sensors | - Critical sensors: space temperature, relative humidity, carbon dioxide, airflow rate. - Detect flatlining, bias, drift, or failure in sensor, or if the sensor is outside of a feasible range. |
| Thermostat occupied/unoccupied cooling/heating set points | Detect if the space cooling/heating set points dead band is not high enough. |
| Thermostat space temperature | Identify if zones are outside of an acceptable temperature range over a period of time. Indicate if the space is over/under cooled/heated or if there is a leaky/stuck VAV damper. |
| VAV supply airflow | - Detect if supply airflow is adequate to the zone (i.e. supply airflow is below the set point while the supply damper is fully open). - Detect if supply airflow is constantly at maximum flow. |
| Chilled Water Plant Faults |  |
| Sensors | - Critical sensors: Chiller, and cooling tower leaving and return water temperatures; chilled water flow rate; pressure. - Detect flatlining, bias, drift, or failure in sensor, or if the sensor is outside of a feasible range. |
| Chilled water plant lockout | Identify if the lockout temperature is too low. |
| Chiller leaving water temperature reset | Identify if the chiller leaving water temperature set point is a fixed value or does not vary through the reset range. |
| Tower leaving water temperature reset | Identify if the tower water temperature set point is a fixed value or does not vary through the reset range. |
| Hydronic differential pressure reset | Identify if the hydronic differential pressure set point is a fixed value or does not vary through the reset range. |
| Chiller short cycling | Identify if the chiller is cycling too frequently. |
| Cooling tower fan cycling | Identify if the fan is cycling too frequently. |
| Hot Water Plant Faults |  |
| Sensors | - Critical sensors: Boiler leaving and return water temperatures; hot water flow rate; pressure. - Detect flatlining, bias, drift, or failure in sensor or if the sensor is outside of a feasible range. |
| Hot water plant lockout | Identify if the lockout temperature is too high or if the boiler is in operation when no heating load exists. |
| Boiler leaving water temperature reset | Identify if the boiler leaving water temperature set point is a fixed value or does not vary through the reset range. |
| Hydronic differential pressure reset | Identify if the hydronic differential pressure set point is a fixed value or does not vary through the reset range. |
| Boiler short cycling | Identify if the boiler cycles on and off too frequently. |

Table 2: Monitoring Action Plan – Fault Detection and Diagnosis