| PROJECT NAME: |  |  |  |  | JOB No. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ATTACHMENT: |  |  |  |  | MR No. |  |  |  |  |  |
| DETAILS |  |  |  |  |  |  |  |  |  |  |
|  | Influent Seawater Supply |  |  |  | Minimum |  |  | Maximum |  |  |
|  | Influent Seawater Volumetric Flowrate |  | (l/s) |  | * |  |  | * |  |  |
|  | Influent Seawater Operational Pressure at Interface (Barg) |  |  |  | * |  |  |  |  |  |
|  | Influent Seawater Shut-off Pressure |  | (Barg) |  | n/a |  |  |  |  |  |
|  | Max. Operational Rate of Change of Seawater Flowrate [(l/s)/min] |  |  |  | n/a |  |  | * |  |  |
|  | Max. Emergency Rate of Change of Seawater Flowrate [(l/s)/min] |  |  |  | n/a |  |  | * |  |  |
|  | Influent Seawater Quality |  |  |  | Minimum |  |  | Maximum |  |  |
|  | Sodium |  | (mg Na/l) |  |  |  |  |  |  |  |
|  | Potassium |  | (mg K/l) |  |  |  |  |  |  |  |
|  | Calcium |  | (mg Ca/l) |  |  |  |  |  |  |  |
|  | Magnesium |  | (mg Mg/l) |  |  |  |  |  |  |  |
|  | Strontium |  | (mg Sr/l) |  |  |  |  |  |  |  |
|  | Barium |  | (mg Ba/l) |  |  |  |  |  |  |  |
|  | Total Boron |  | (mg B/l) |  |  |  |  |  |  |  |
|  | Total Iron |  | (mg Fe/l) |  |  |  |  |  |  |  |
|  | Total Aluminium |  | (mg Al/l) |  |  |  |  |  |  |  |
|  | Total Manganese |  | (mg Mn/l) |  |  |  |  |  |  |  |
|  | Chloride |  | (mg Cl/l) |  |  |  |  |  |  |  |
|  | Sulfate |  | (mg SO4/l) |  |  |  |  |  |  |  |
|  | Bromide |  | (mg Br/l) |  |  |  |  |  |  |  |
|  | Fluoride |  | (mg F/l) |  |  |  |  |  |  |  |
|  | Total Inorganic Nitrogen |  | (mg N/l) |  |  |  |  |  |  |  |
|  | Bicarbonate |  | (mg HCO3/l) |  |  |  |  |  |  |  |
|  | Carbon Dioxide |  | (mg CO2/l) |  |  |  |  |  |  |  |
|  | pH |  |  |  |  |  |  |  |  |  |
|  | Total Dissolved Solids |  | (mg tds/l) |  |  |  |  |  |  |  |
|  | Suspended Solids |  | (mg ss/l) |  |  |  |  |  |  |  |
|  | Total Organic Carbon |  | (mg C/l) |  |  |  |  |  |  |  |
|  | Temperature |  | (°C) |  |  |  |  |  |  |  |
|  | Assimilable Organic Carbon |  | (mg C/l) |  |  |  |  |  |  |  |
|  | Total Coliforms (Prior to Chlorine Addition) |  | (mpn/100 ml) |  |  |  |  |  |  |  |
|  | Normal Free Chlorine Concentration |  | (mg Cl2/l) |  |  |  |  |  |  |  |
|  | Shock Chlorination Free Chlorine Concentration |  | (mg Cl2/l) |  |  |  |  |  |  |  |
|  | Shock Chlorination Duration |  | (mins) |  |  |  |  |  |  |  |
|  | Interval Between Shock Chlorination Events |  | (hrs) |  |  |  |  | n/a |  |  |
|  | Screening Size |  | (mm) |  | n/a |  |  |  |  |  |
|  | Number of Seawater Supply Mains |  |  |  |  |  |  |  |  |  |
|  | Seawater Supply Termination Point Details |  |  |  |  |  |  |  |  |  |
|  | Type of Termination to be Supplied by Seller |  |  |  |  |  |  |  |  |  |
|  | Connection at Termination Point to be Made by |  |  |  |  |  |  |  |  |  |
|  | Nominal Pipe Size at Termination Point |  | (mm) |  |  |  |  |  |  |  |
|  | Pipe Material and Schedule at Termination Point |  |  |  |  |  |  |  |  |  |
|  | Product Water Production |  |  |  | Minimum |  |  | Maximum |  |  |
|  | Total Production of Distilled Water |  | Ml/day |  |  |  |  |  |  |  |
|  | Distilled Water Production Tolerance |  | Ml/day |  |  |  |  |  |  |  |
|  | Distilled Water Pressure at Interface |  | (Barg) |  |  |  |  |  |  |  |
|  | Max. Rate of Change of Distilled Water Flowrate Setpoint (Ml/day)/min |  |  |  | n/a |  |  |  |  |  |
|  | Minimum Single Unit Production (Turndown) |  | Ml/day |  |  |  |  | n/a |  |  |
|  | Minimum Total Plant Production (Turndown) |  | Ml/day |  |  |  |  | n/a |  |  |
|  | Product Water Quality |  |  |  | Required |  |  | Guaranteed |  |  |
|  | Total Dissolved Solids |  | (mg tds/l) |  |  |  |  | * |  |  |
|  | Sodium |  | (mg Na/l) |  |  |  |  | * |  |  |
|  | Chloride |  | (mg Cl/l) |  |  |  |  | * |  |  |
|  | Total Boron |  | (mg B/l) |  |  |  |  | * |  |  |
|  | pH |  |  |  |  |  |  | * |  |  |
|  | Maximum Temperature |  | (°C) |  |  |  |  | * |  |  |
|  | Number of Distilled Water Supply Mains |  |  |  |  |  |  |  |  |  |
|  | Distilled Water Termination Point Details |  |  |  |  |  |  |  |  |  |
|  | Type of Termination to be Supplied by Seller |  |  |  |  |  |  |  |  |  |
|  | Connection at Termination Point to be Made by |  |  |  |  |  |  |  |  |  |
|  | Nominal Pipe Size at Termination Point |  | (mm) |  |  |  |  |  |  |  |
|  | Pipe Material and Schedule at Termination Point |  |  |  |  |  |  |  |  |  |
|  | Low Pressure Steam System |  |  |  | Minimum |  |  | Maximum |  |  |
|  | Steam Flowrate Available |  | (kg/s) |  |  |  |  |  |  |  |
|  | Steam Pressure Available |  | (bara) |  |  |  |  |  |  |  |
|  | Steam Flowrate Required |  | (kg/s) |  | * |  |  | * |  |  |
|  | Steam Pressure Required |  | (bara) |  | * |  |  | * |  |  |
|  | Maximum Rate of Change of Steam Flowrate Set Point [(kg/s)/hr] |  |  |  | n/a |  |  |  |  |  |
|  | Maximum Deviation Between Actual and Set Point Flowrate (kg/s) |  |  |  | n/a |  |  |  |  |  |
|  | Lag in System Response to Flowrate Set Point Changes (s) |  |  |  | n/a |  |  |  |  |  |
|  | System Response Time Constant for Flowrate Set Point Changes (s) |  |  |  | n/a |  |  |  |  |  |
|  | Superheat |  | (°C) |  |  |  |  |  |  |  |
|  | Quality (Mass Fraction Steam) |  |  |  |  |  |  |  |  |  |
|  | Desuperheating Water Flow Required |  | (kg/s) |  | * |  |  | * |  |  |
|  | Number of Steam Headers |  |  |  |  |  |  |  |  |  |
|  | LP Steam Termination Point Details |  |  |  |  |  |  |  |  |  |
|  | Type of Termination to be Supplied by Seller |  |  |  |  |  |  |  |  |  |
|  | Connection at Termination Point to be Made by |  |  |  |  |  |  |  |  |  |
|  | Nominal Pipe Size at Termination Point |  | (mm) |  |  |  |  |  |  |  |
|  | Pipe Material and Schedule at Termination Point |  |  |  |  |  |  |  |  |  |
|  | Medium Pressure Steam System |  |  |  | Minimum |  |  | Maximum |  |  |
|  | Steam Flowrate Available |  | (kg/s) |  |  |  |  |  |  |  |
|  | Steam Pressure Available |  | (bara) |  |  |  |  |  |  |  |
|  | Maximum Rate of Change of Steam Flowrate Available [(kg/s)/hr] |  |  |  | n/a |  |  |  |  |  |
|  | Superheat Available |  | (°C) |  |  |  |  |  |  |  |
|  | Quality Available (Mass Fraction Steam) |  |  |  |  |  |  |  |  |  |
|  | Steam Flowrate Required |  | (kg/s) |  | * |  |  | * |  |  |
|  | Steam Pressure |  | (Bara) |  | * |  |  | * |  |  |
|  | Maximum Rate of Change of Steam Flowrate Required [(kg/s)/hr] |  |  |  | n/a |  |  | * |  |  |
|  | Superheat Required |  | (°C) |  | * |  |  | * |  |  |
|  | Quality | (Mass Fraction Steam) |  |  | * |  |  | * |  |  |
|  | Desuperheating Water Flow Required |  | (kg/s) |  | * |  |  | * |  |  |
|  | Number of Medium Pressure Steam Headers |  |  |  |  |  |  |  |  |  |
|  | MP Steam Termination Point Details |  |  |  |  |  |  |  |  |  |
|  | Type of Termination to be Supplied by Seller |  |  |  |  |  |  |  |  |  |
|  | Connection at Termination Point to be Made by |  |  |  |  |  |  |  |  |  |
|  | Nominal Pipe Size at Termination Point |  | (mm) |  |  |  |  |  |  |  |
|  | Pipe Material and Schedule at Termination Point |  |  |  |  |  |  |  |  |  |
|  | Desuperheating Water System |  |  |  | Minimum |  |  | Maximum |  |  |
|  | Desuperheating Water Flow Rate Available |  | l/s |  |  |  |  |  |  |  |
|  | Desuperheating Water Pressure Available at Interface (barg) |  |  |  |  |  |  |  |  |  |
|  | Desuperheating Water Flow Rate Required |  | l/s |  | * |  |  | * |  |  |
|  | Desuperheating Water Pressure Required |  | (barg) |  | * |  |  | * |  |  |
|  | Number of Desuperheating Water Headers Required |  |  |  | * |  |  |  |  |  |
|  | Desuperheating Water Termination Point Details |  |  |  |  |  |  |  |  |  |
|  | Type of Termination to be Supplied by Seller |  |  |  |  |  |  |  |  |  |
|  | Connection at Termination Point to be Made by |  |  |  |  |  |  |  |  |  |
|  | Nominal Pipe Size at Termination Point |  | (mm) |  |  |  |  |  |  |  |
|  | Pipe Material and Schedule at Termination Point |  |  |  |  |  |  |  |  |  |
|  | Condensate Return |  |  |  | Minimum |  |  | Maximum |  |  |
|  | Condensate Return Flowrate |  | (l/s) |  | * |  |  | * |  |  |
|  | Condensate Return Temperature |  | (°C) |  | * |  |  | * |  |  |
|  | Condensate Return Pressure at Interface |  | (Bara) |  |  |  |  |  |  |  |
|  | Maximum Rate of Change of Condensate Return |  | (l/s)/min) |  | n/a |  |  |  |  |  |
|  | Condensate Return Water Quality |  |  |  |  |  |  |  |  |  |
|  | Maximum Conductivity |  | (µS/cm) |  |  |  |  |  |  |  |
|  | Maximum Dissolved Oxygen |  | (mg O2/l) |  |  |  |  |  |  |  |
|  | Maximum Dissolved Carbon Dioxide |  | (mg CO2/l) |  |  |  |  |  |  |  |
|  | pH |  |  |  |  |  |  |  |  |  |
|  | Number of Condensate Return Lines |  |  |  |  |  |  |  |  |  |
|  | Condensate Return Termination Point Details |  |  |  |  |  |  |  |  |  |
|  | Type of Termination to be Supplied by Seller |  |  |  |  |  |  |  |  |  |
|  | Connection at Termination Point to be Made by |  |  |  |  |  |  |  |  |  |
|  | Nominal Pipe Size at Termination Point |  | (mm) |  |  |  |  |  |  |  |
|  | Pipe Material and Schedule at Termination Point |  |  |  |  |  |  |  |  |  |
|  | Cooling Water Return |  |  |  | Minimum |  |  | Maximum |  |  |
|  | Cooling Water Return Flowrate |  | (l/s) |  | * |  |  | * |  |  |
|  | Cooling Water Return Pressure at Interface |  | (bara) |  |  |  |  |  |  |  |
|  | Cooling Water Return Temperature Control |  |  |  |  |  |  |  |  |  |
|  | Temperature Control Required/Not Required |  |  |  |  |  |  |  |  |  |
|  | Cooling Water Return Temperature Setpoint |  | (°C) |  |  |  |  |  |  |  |
|  | Return Temperature Setpoint Compared to Inlet |  | (°C) |  |  |  |  |  |  |  |
|  | Maximum Rate of Change of Cooling Water Return Set Point (°C/min) |  |  |  |  |  |  |  |  |  |
|  | Maximum Tolerance of Actual to Set Point Temperature |  |  | (°C) |  |  |  |  |  |  |
|  | Maximum Cooling Water Return Temperature |  | (°C) |  |  |  |  |  |  |  |
|  | Maximum Increase in Return Temperature Compared to Inlet |  |  | (°C) |  |  |  |  |  |  |
|  | Cooling Water Return Quality |  |  |  |  |  |  |  |  |  |
|  | Maximum Total Iron |  | (mg Fe/l) |  |  |  |  |  |  |  |
|  | Maximum Total Nickel |  | (mg Ni/l) |  |  |  |  |  |  |  |
|  | Maximum Total Chrome |  | (mg Cr/l) |  |  |  |  |  |  |  |
|  | Maximum Total Copper |  | (mg Cu/l) |  |  |  |  |  |  |  |
|  | Maximum Total Manganese |  | (mg Mn/l) |  |  |  |  |  |  |  |
|  | Cooling Water Additives |  |  |  | Add 1 | Add 2 | Add 3 | Add 4 | Add 5 | Add 6 |
|  | Additive Trade Name |  |  |  | * | * | * | * | * | * |
|  | Additive Chemical Formula |  |  |  | * | * | * | * | * | * |
|  | Maximum Concentration of Chemical in Cooling Water Return (mg/l) |  |  |  | * | * | * | * | * | * |
|  | Purpose of Chemical Addition |  |  |  | * | * | * | * | * | * |
|  | Maximum pH of Cooling Water Return |  |  |  | * | * | * | * | * | * |
|  | Minimum pH of Cooling Water Return |  |  |  | * | * | * | * | * | * |
|  | Number of Cooling Seawater Return Lines |  |  |  |  |  |  |  |  |  |
|  | Cooling Water Return Termination Point Details |  |  |  |  |  |  |  |  |  |
|  | Type of Termination to be Supplied by Seller |  |  |  |  |  |  |  |  |  |
|  | Connection at Termination Point to be Made by |  |  |  |  |  |  |  |  |  |
|  | Nominal Pipe Size at Termination Point (mm) |  |  |  |  |  |  |  |  |  |
|  | Pipe Material and Schedule at Termination Point |  |  |  |  |  |  |  |  |  |
|  | Brine Discharge |  |  |  | Minimum |  |  | Maximum |  |  |
|  | Brine Discharge Flowrate (l/s) |  |  |  | * |  |  | * |  |  |
|  | Brine Discharge Pressure at Interface (Barg) |  |  |  |  |  |  |  |  |  |
|  | Maximum Brine Temperature (°C) |  |  |  |  |  |  |  |  |  |
|  | Maximum Increase in Brine Temp. Compared to Inlet Seawater (°C) |  |  |  |  |  |  |  |  |  |
|  | Brine Discharge Quality |  |  |  | Minimum |  |  | Maximum |  |  |
|  | Total Dissolved Solids (mg/l) |  |  |  | * |  |  | * |  |  |
|  | pH |  |  |  | * |  |  | * |  |  |
|  | Maximum Total Iron (mg Fe/l) |  |  |  |  |  |  |  |  |  |
|  | Maximum Total Nickel (mg Ni/l) |  |  |  |  |  |  |  |  |  |
|  | Maximum Total Chrome (mg Cr/l) |  |  |  |  |  |  |  |  |  |
|  | Maximum Total Copper (mg Cu/l) |  |  |  |  |  |  |  |  |  |
|  | Maximum Total Manganese (mg Mn/l) |  |  |  |  |  |  |  |  |  |
|  | Brine Discharge Additives |  |  |  | Add 1 | Add 2 | Add 3 | Add 4 | Add 5 | Add 6 |
|  | Additive Trade Name |  |  |  | * | * | * | * | * | * |
|  | Additive Chemical Formula |  |  |  | * | * | * | * | * | * |
|  | Maximum Concentration of Chemical in Brine Discharge (mg/l) |  |  |  | * | * | * | * | * | * |
|  | Purpose of Chemical Addition |  |  |  | * | * | * | * | * | * |
|  | Number of Brine Discharge Lines |  |  |  |  |  |  |  |  |  |
|  | Brine Discharge Termination Point Details |  |  |  |  |  |  |  |  |  |
|  | Type of Termination to be Supplied by Subcontractor |  |  |  |  |  |  |  |  |  |
|  | Connection at Termination Point to be Made by |  |  |  |  |  |  |  |  |  |
|  | Nominal Pipe Size at Termination Point |  | (mm) |  |  |  |  |  |  |  |
|  | Pipe Material and Schedule at Termination Point |  |  |  |  |  |  |  |  |  |
|  | MED Design Conditions |  |  |  |  |  |  |  |  |  |
|  | Stream Temperatures |  |  |  |  |  |  |  |  |  |
|  | Top brine temperature for design production |  | (°C) |  | * |  |  |  |  |  |
|  | Max distillate design temperature |  | (°C) |  | * |  |  |  |  |  |
|  | Max cooling/brine water discharge temperature to sea (°C) |  |  |  | * |  |  |  |  |  |
|  | Max difference brine/cooling - seawater temperature (°C) |  |  |  | * |  |  |  |  |  |
|  | Miscellaneous |  |  |  |  |  |  |  |  |  |
|  | Max salinity at the top brine temperature |  | g/kg |  | * |  |  |  |  |  |
|  | Max content of copper in distillate |  | mg/kg |  | * |  |  |  |  |  |
|  | Operating period between successive tube cleanings Hours |  |  |  | * |  |  |  |  |  |
|  | Lifetime of paint system of MED |  | years |  | * |  |  |  |  |  |
|  | Maximum drain down time for MED unit |  | hrs |  | * |  |  |  |  |  |
|  | Capacity in excess of design production for distillate trays & ducts % |  |  |  | * |  |  |  |  |  |
|  | Manhole diameter for MED access |  | mm |  | * |  |  |  |  |  |
|  | Condenser Tube Velocity |  | (m/s) |  | * |  |  |  |  |  |
|  | MED Details |  |  |  |  |  |  |  |  |  |
|  | Number of MED Units offered / minimum number of units acceptable |  |  |  | * |  |  |  |  |  |
|  | Unit Dimensions |  |  |  |  |  |  |  |  |  |
|  | Unit length |  | m |  | * |  |  |  |  |  |
|  | Unit width |  | m |  | * |  |  |  |  |  |
|  | Unit Height |  | m |  | * |  |  |  |  |  |
|  | Overall Height |  | m |  | * |  |  |  |  |  |
|  | Minimum Headroom below distiller |  | m |  | * |  |  |  |  |  |
|  | Effect Details |  |  |  |  |  |  |  |  |  |
|  | Effect No |  |  |  | * | * | * | * | * | * |
|  | Number of cells per effect |  |  |  | * | * | * | * | * | * |
|  | Length of each cell |  | (m) |  | * | * | * | * | * | * |
|  | Width of ech cell |  | (m) |  | * | * | * | * | * | * |
|  | Height of each cell |  | (m) |  | * | * | * | * | * | * |
|  | Number of tubes in cell with top row material |  |  |  | * | * | * | * | * | * |
|  | Top tube material UNS number |  |  |  | * | * | * | * | * | * |
|  | Number of tubes with top row material |  |  |  | * | * | * | * | * | * |
|  | Top Tube Wall Thickness |  | (mm) |  | * | * | * | * | * | * |
|  | Top Length of Tube |  | (mm) |  | * | * | * | * | * | * |
|  | Top outside diameter of Tube |  | (mm) |  | * | * | * | * | * | * |
|  | Heat exchange area on the outside of top row material tubes (m2) |  |  |  | * | * | * | * | * | * |
|  | Top tube material corrosion/erosion allowance |  | (mm) |  | * | * | * | * | * | * |
|  | Remaining tube material UNS number |  |  |  | * | * | * | * | * | * |
|  | Remaining tube wall thickness |  | (mm) |  | * | * | * | * | * | * |
|  | Remaining length of tube |  | (mm) |  | * | * | * | * | * | * |
|  | Remaining tubes outside diameter of tube |  | (mm) |  | * | * | * | * | * | * |
|  | Heat exchange area on the outside of tubes |  | (m2) |  | * | * | * | * | * | * |
|  | Remaining tube material corrosion/erosion allowance (mm) |  |  |  | * | * | * | * | * | * |
|  | Tube Sheet Material |  | UNS Number |  | * | * | * | * | * | * |
|  | Tube Sheet Thickness |  | (mm) |  | * | * | * | * | * | * |
|  | Intermediate tube support plates material |  | UNS Number |  | * | * | * | * | * | * |
|  | Intermediate tube support plates thickness |  | (mm) |  | * | * | * | * | * | * |
|  | Tube sheet material corrosion/erosion allowance |  | (mm) |  | * | * | * | * | * | * |
|  | Demister mat material |  | UNS Number |  | * | * | * | * | * | * |
|  | Demister mat thickness |  | (mm) |  | * | * | * | * | * | * |
|  | Shell Wall Material |  | UNS Number |  | * |  |  |  |  |  |
|  | Shell wall Thickness |  | (mm) |  | * |  |  |  |  |  |
|  | Shell Wall Cladding Material |  | UNS Number |  | * |  |  |  |  |  |
|  | Shell Wall Cladding Thickness |  | (mm) |  | * |  |  |  |  |  |
|  | Shell External Reinforcement Material |  | UNS Number |  | * |  |  |  |  |  |
|  | Shell wall cladding material corrosion/erosion allowance (mm) |  |  |  | * |  |  |  |  |  |
|  | External Vapor Boxes Material |  | UNS Number |  | * |  |  |  |  |  |
|  | External Vapor Boxes Thickness |  | (mm) |  | * |  |  |  |  |  |
|  | External vapor box material corrosion/erosion allowance (mm) |  |  |  | * |  |  |  |  |  |
|  | Spray Nozzles Material |  |  |  | * |  |  |  |  |  |
|  | Distilled Waterbox Material |  | UNS Number |  | * |  |  |  |  |  |
|  | Thickness of Distilled Waterbox Material |  | (mm) |  | * |  |  |  |  |  |
|  | Distilled Waterbox Material Corrosion/Erosion Allowance (mm) |  |  |  | * |  |  |  |  |  |
|  | Condenser Shell Material |  |  |  | * |  |  |  |  |  |
|  | Condenser shell wall Thickness |  | (mm) |  | * |  |  |  |  |  |
|  | Condenser shell wall cladding material |  | UNS Number |  | * |  |  |  |  |  |
|  | Condenser shell wall cladding thickness |  | (mm) |  | * |  |  |  |  |  |
|  | Condenser shell wall cladding material corrosion/erosion allow (mm) |  |  |  | * |  |  |  |  |  |
|  | Condenser external reinforcement material |  | UNS Number |  | * |  |  |  |  |  |
|  | Condenser waterbox material |  | UNS Number |  | * |  |  |  |  |  |
|  | Condenser water box thickness |  | (mm) |  | * |  |  |  |  |  |
|  | Condenser waterbox cladding material |  | UNS Number |  | * |  |  |  |  |  |
|  | Condenser waterbox cladding thickness |  | (mm) |  | * |  |  |  |  |  |
|  | Condenser waterbox cladding material corrosion/erosion allow (mm) |  |  |  | * |  |  |  |  |  |
|  | Thermo compressor steam transfer From Effect/ To Effect |  |  |  | * |  |  | * |  |  |
|  | Thermo compressor suction materials |  | Uns Number |  | * |  |  |  |  |  |
|  | Thermo compressor nozzles material |  | Uns Number |  | * |  |  |  |  |  |
|  | Thermo compressor pipe material Suction/ Discharge Uns Number |  |  |  | * |  |  | * |  |  |
|  | Thermo compressor pipe schedule Suction/ Discharge |  |  |  | * |  |  | * |  |  |
|  | Bolt Material / Nut Material inside evaporator |  | UNS Number |  | * |  |  | * |  |  |
|  | Bolt Material / Nut Material on evaporator |  | UNS Number |  | * |  |  | * |  |  |
|  | Bolt Material / Nut Material on piping |  | UNS Number |  | * |  |  | * |  |  |
|  | Bolt Material / Nut Material on vent condenser |  | UNS Number |  | * |  |  | * |  |  |
|  | Bolt Material / Nut Material reject condenser |  | UNS Number |  | * |  |  | * |  |  |
|  | Bolt Material / Nut Material on Vent condenser |  | UNS Number |  | * |  |  | * |  |  |
|  | Seawater / Brine Isolating valves material valve type/body/internals |  |  |  | * |  | * |  | * |  |
|  | Seawater / Brine control valves material valve type/body/internals |  |  |  | * |  | * |  | * |  |
|  | Distillate Isolating valves material valve type/body/internals |  |  |  | * |  | * |  | * |  |
|  | Distillate control valve material valve type/body/internals |  |  |  | * |  | * |  | * |  |
|  | Steam Isolating valves material valve type/body/internals |  |  |  | * |  | * |  | * |  |
|  | Steam control valve material valve type/body/internals |  |  |  | * |  | * |  | * |  |
|  | Drains and vents material (size <50 mm) valve type/body/internals |  |  |  | * |  | * |  | * |  |
|  | Seawater pipe schedule / material |  |  |  | * |  |  | * |  |  |
|  | Brine pipe schedule / material |  |  |  | * |  |  | * |  |  |
|  | Distillate pipe schedule / material |  |  |  | * |  |  | * |  |  |
|  | Steam pipe schedule / material |  |  |  | * |  |  | * |  |  |
|  | Seawater Makeup Filters |  |  |  |  |  |  |  |  |  |
|  | Type / Manufacturer |  |  |  | * |  |  | * |  |  |
|  | Aperture size |  | mm x mm |  | * |  |  | * |  |  |
|  | Frame material |  | UNS Number |  | * |  |  |  |  |  |
|  | Seawater contact materials |  | UNS Number |  | * |  |  |  |  |  |
|  | Screenings contact material |  | UNS Number |  | * |  |  |  |  |  |
|  | Vacuum System (per MED Unit) |  |  |  |  |  |  |  |  |  |
|  | Ejector/Condenser configuration |  |  |  | * |  |  |  |  |  |
|  | (PC = Pre Condenser, E = Ejector, AC = After Condenser) |  |  |  |  |  |  |  |  |  |
|  | Air leakage rate, number of times design leakage |  |  |  | * |  |  |  |  |  |
|  | Min vapor extracted as % of vapor produced in extracted stages % |  |  |  | * |  |  |  |  |  |
|  | Start-up ejector system pressure |  | mbar |  | * |  |  |  |  |  |
|  | Start-up ejector system to achieve above pressure |  | hrs |  | * |  |  |  |  |  |
|  | Condenser Shell material, PREN Number / UNS Number |  |  |  | * |  |  | * |  |  |
|  | Condenser shell wall cladding material corrosion/erosion allow. (mm) |  |  |  | * |  |  |  |  |  |
|  | Condenser Nozzle, diffusers PREN Number / UNS Number |  |  |  | * |  |  | * |  |  |
|  | Condenser Drain piping, schedule / material UNS number |  |  |  | * |  |  | * |  |  |
|  | Pipework from vent condenser to ejector, schedule/material UNS No. |  |  |  | * |  |  | * |  |  |
|  | Pipework from ejector to vent condenser, schedule/material UNS No. |  |  |  | * |  |  | * |  |  |
|  | Ejector nozzle material, UNS Number |  |  |  | * |  |  |  |  |  |
|  | Ejector Nozzle Holder Material, UNS Number |  |  |  | * |  |  |  |  |  |
|  | Suction chamber material, UNS Number |  |  |  | * |  |  |  |  |  |
|  | Diffuser material, UNS Number |  |  |  | * |  |  |  |  |  |
|  | Suction piping, size / schedule / material UNS Number |  |  |  | * |  | * |  | * |  |
|  | Discharge piping, size / schedule / material UNS Number |  |  |  | * |  | * |  | * |  |
|  | Deaerator |  |  |  |  |  |  |  |  |  |
|  | Deaerator Storage Tank Retention Time based on feed flow mins |  |  |  | * |  |  |  |  |  |
|  | Deaerator drainage pipework – MATERIAL |  |  |  | * |  |  |  |  |  |
|  | Deaerator Vessel / Storage Tank - MATERIAL |  |  |  | * |  |  | * |  |  |
|  | Deaerator Vessel / Storage Tank - MATERIAL THICKNESS (mm) |  |  |  | * |  |  | * |  |  |
|  | Deaerator Cladding material above packing, UNS number |  |  |  | * |  |  |  |  |  |
|  | Deaerator Cladding thickness |  | (mm) |  | * |  |  |  |  |  |
|  | Deaeratorl cladding material corrosion/erosion allowance (mm) |  |  |  | * |  |  |  |  |  |
|  | Deaerator Cladding material below packing, UNS Number |  |  |  | * |  |  |  |  |  |
|  | Seawater distribution pipe material UNS Number |  |  |  | * |  |  |  |  |  |
|  | Seawater spray nozzle material UNS Number |  |  |  | * |  |  |  |  |  |
|  | Seawater splash plate material UNS Number |  |  |  | * |  |  |  |  |  |
|  | Steam stripping distributor material UNS Number |  |  |  | * |  |  |  |  |  |
|  | Steam Pipe from Evaporator to deaerator, size/sched/material UNS No. |  |  |  | * |  | * |  | * |  |
|  | Demister material UNS Number |  |  |  | * |  |  |  |  |  |
|  | Gratings material UNS Number |  |  |  | * |  |  |  |  |  |
|  | Deaerator Type (Packing or Tray) |  |  |  |  |  |  |  |  |  |
|  | Packing / Tray - MATERIAL |  |  |  | * |  |  |  |  |  |
|  | Stubs and flanges of drain connections, material UNS Number |  |  |  | * |  |  |  |  |  |
|  | Stubs and flanges of vent connections, material UNS Number |  |  |  | * |  |  |  |  |  |
|  | Isolating valve material UNS Number |  |  |  | * |  |  |  |  |  |
|  | All internal surfaces under crevices material UNS Number |  |  |  | * |  |  |  |  |  |
|  | Chemical Cleaning |  |  |  |  |  |  |  |  |  |
|  | Tube Cleaning chemical Name / Concentration |  |  |  | * |  |  | * |  |  |
|  | Corrosion inhibitor Name / Concentration |  |  |  | * |  |  | * |  |  |
|  | Cleaning Pipework Material |  |  |  | * |  |  |  |  |  |
|  | Chemical Wash Volume |  | m3 |  | * |  |  |  |  |  |
|  | Antiscalant Dosing |  |  |  |  |  |  |  |  |  |
|  | Anti Scalant type |  |  |  | * |  |  |  |  |  |
|  | Minimum & Maximum dose rate capability antiscale mg/l |  |  |  | * |  |  | * |  |  |
|  | Antiscalant Dose at top brine temperature |  | mg/l |  | * |  |  |  |  |  |
|  | Antiscalant make up and dosing tank material |  |  |  | * |  |  |  |  |  |
|  | Number Dosing pumps per MED unit No. duty/ No. standby |  |  |  |  |  |  |  |  |  |
|  | Dosing pipework Material |  |  |  | * |  |  |  |  |  |
|  | Average dose /Average storage time mg/l / Days |  |  |  | * |  |  | * |  |  |
|  | Maximum dose /Maximum storage time mg/l / Days |  |  |  | * |  |  | * |  |  |
|  | Design discharge pressure for dosing pump |  | bara |  | * |  |  |  |  |  |
|  | Antifoaming Dosing |  |  |  |  |  |  |  |  |  |
|  | Minimum & Maximum dose rate capability antifoam mg/l |  |  |  | * |  |  | * |  |  |
|  | Normal dose rate of antifoam |  | mg/l |  | * |  |  |  |  |  |
|  | Antifoam makeup and dosing tank material |  |  |  | * |  |  |  |  |  |
|  | Dosing pipework Material |  |  |  | * |  |  |  |  |  |
|  | Average dose /Average storage time mg/l / Days |  |  |  | * |  |  | * |  |  |
|  | Maximum dose /Maximum storage time mg/l / Days |  |  |  | * |  |  | * |  |  |
|  | Design discharge pressure for dosing pump |  | bara |  | * |  |  |  |  |  |
|  | General Dosing Tank Information |  |  |  |  |  |  |  |  |  |
|  | Dosing Tank height above floor for draining |  | mm |  | * |  |  |  |  |  |
|  | Mixing time to achieve fully mixed |  | mins |  | * |  |  |  |  |  |
|  | Max Speed of the agitator |  | rpm |  | * |  |  |  |  |  |
|  | Number of portable drum pumps required antiscalant/ antifoam |  |  |  |  |  |  |  |  |  |
|  | Method of Examination of parts (name parts) |  |  |  |  |  |  |  |  |  |
|  | Radiographic |  |  |  | * |  |  |  |  |  |
|  | Ultrasonic |  |  |  | * |  |  |  |  |  |
|  | Magnetic Particle |  |  |  | * |  |  |  |  |  |
|  | Liquid penetrant |  |  |  | * |  |  |  |  |  |
|  | Method of Examination of parts (name parts) |  |  |  |  |  |  |  |  |  |
|  | Radiographic |  |  |  | * |  |  |  |  |  |
|  | Ultrasonic |  |  |  | * |  |  |  |  |  |
|  | Magnetic Particle |  |  |  | * |  |  |  |  |  |
|  | Liquid penetrant |  |  |  | * |  |  |  |  |  |
|  | Production Cases |  |  |  | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 |
|  | Feed Water Temperature |  | (°C) |  |  |  |  |  |  |  |
|  | Top Brine Temperature |  | (°C) |  | * | * | * | * | * | * |
|  | Fouling Status |  |  |  |  |  |  |  |  |  |
|  | Fouling Factor Used |  | (m2.K/w) |  | * | * | * | * | * | * |
|  | Distillate Production |  | kg/s |  | * | * | * | * | * | * |
|  | Heat Reject Cooling Water feed |  | kg/s |  | * | * | * | * | * | * |
|  | Heat Reject Discharge Temperature |  | kg/s |  | * | * | * | * | * | * |
|  | Heat Reject flow rate to Outfall |  | kg/s |  | * | * | * | * | * | * |
|  | Last stage Brine Temperature |  | (°C) |  | * | * | * | * | * | * |
|  | Final Brine blowdown discharge flowrate |  | kg/s |  | * | * | * | * | * | * |
|  | Total flow to outfall |  | kg/s |  | * | * | * | * | * | * |
|  | Temperature to Outfall |  | (°C) |  | * | * | * | * | * | * |
|  | Total Dissolved solids in brine from first effect |  | (g/l) |  | * | * | * | * | * | * |
|  | Total Dissolved solids in final brine discharge |  | (g/l) |  | * | * | * | * | * | * |
|  | Makeup flow to the MED |  | kg/s |  | * | * | * | * | * | * |
|  | Discharge pressure of Brine Recirculation Pump |  | (barg) |  | * | * | * | * | * | * |
|  | Pressure of Heat reject cooling Water at interface |  | (barg) |  | * | * | * | * | * | * |
|  | Discharge Pressure of Heat Reject flow at interface (barg) |  |  |  | * | * | * | * | * | * |
|  | Reject Brine Discharge pressure at interface |  | (barg) |  |  |  |  |  |  |  |
|  | Power Consumption (kWh/m3 distillate) |  |  |  | * | * | * | * | * | * |
|  | Heat Demand Without Ejector System |  | (kJ/kg distillate) |  | * | * | * | * | * | * |
|  | Heat Demand for Vacuum and vent system |  | (kJ/kg distillate) |  | * | * | * | * | * | * |
|  | Total heat demand |  | (kJ/kg distillate) |  | * | * | * | * | * | * |
|  | Antiscale Additive Specific Consumption |  | (kg/kg distillate) |  | * | * | * | * | * | * |
|  | Antifoam Additive Specific Consumption |  | (kg/kg distillate) |  | * | * | * | * | * | * |
|  | Required Electrical Information |  |  |  |  |  |  |  |  |  |
|  | Electrical Power Demand |  | (A / V) |  | * |  | @ |  | * |  |
|  | Power Required: Target / Guarantee Case |  | (KW / KW) |  |  |  |  | * |  |  |
|  | List electrical 3-phase motor drives requiring starters by Buyer |  |  |  | Motor Description |  |  |  |  | HP |
|  |  |  |  |  | * |  |  |  |  | * |
|  |  |  |  |  | * |  |  |  |  | * |
|  |  |  |  |  | * |  |  |  |  | * |
|  |  |  |  |  | * |  |  |  |  | * |
|  |  |  |  |  | * |  |  |  |  | * |
| NOTES: - Specialist shall replace all * (asterisks) and incomplete check boxes with appropriate information. |  |  |  |  |  |  |  |  |  |  |