Centrifugal Fire Pump Acceptance Test Form

Information on this form covers the minimum requirements of NFPA 20 for performing acceptance tests on pumps with electric motors or diesel engine drivers. Other forms are available for periodic inspection, testing, and maintenance.

Owner :

Owner’s Address :

Property on which pump is installed:

Property Address :

Date of Test :

Demand(s) of Fire Protection Systems Supplied By Pump :

Pump :         ☐   Horizontal        ☐    Vertical

Manufacturer : 	               Shop/ Serial Number :

Model or Type :

Rated GPM :	                   Rated Pressure: 	 Rated RPM:

Suction From: 	           If Tank, Size and Height:

Driver:          ☐   Electric  Motor           ☐    Diesel Engineer

Manufacturer:	              Shop/Serial Number:

Model or Type:

Rated Horsepower:	   	  Rated Speed:

If Electric Motor, Rated Voltage: 	             Operating Voltage:

Rated Amperes: 	  Phase Cycles: 	  Service Factor:

Controller Manufacturer:

Shop/Serial Number:		   Model or Type:

Jockey ump on System? ☐  Yes  ☐  No      Setting: On ☐    Off ☐

All questions are to be assumed Yes, No, or Not Applicable

All No answers are to be explained in the comments portion of this form

I. Flush Test (Conduct before Hydrostatic Test)

Suction piping was flushed at 	   gpm?    	☐ Yes   ☐  No   ☐  N/A

(See Table 14.1.1.1 of NFPA 20 2013)

Certificate presented showing flush test?           	☐ Yes   ☐  No   ☐  N/A

II. Hydrostatic Test

Piping tested at 	psi for 2 hours?       	☐ Yes   ☐  No   ☐  N/A

(Note: NFPA 20 requires 200 psi or 50 psi above maximum system pressure whichever is greater)

Piping passed test?      			☐ Yes   ☐  No   ☐  N/A

Certificate presented showing test?		☐ Yes   ☐  No   ☐  N/A

III. People Present

Were the following present to witness the test?

A. Pump manufacturer/representative	☐ Yes   ☐  No   ☐  N/A

B. Engine manufacturer/representative	☐ Yes   ☐  No   ☐  N/A

C. Controller manufacturer/representative	☐ Yes   ☐  No   ☐  N/A

D. Transfer Switch manufacturer/rep.		☐ Yes   ☐  No   ☐  N/A

E. Authority Having Jurisdiction/rep.		☐ Yes   ☐  No   ☐  N/A

IV. Electric Wiring

Was all electric wiring including control inter-wiring for multiple pumps, emergency power supply system, and the jockey pump system completed and checked by the electrical contractor prior to the initial start-up and acceptance test?				☐ Yes   ☐  No   ☐  N/A

V. Flow Test

Run the pump at no-load, rated load, and peak load (usually 150% of the rated load) conditions. For variable speed drivers, run the test with the pressure limiting control “on” at 25, 50, 75, 100, 125, and 150% of rated load and then again at rated speed with the pump isolated from the fire protection system and the relief valve closed.

A. Was the manufacturers certified pump test curve available for comparison to

the acceptance test?			☐ Yes   ☐  No   ☐  N/A

B. Equipment and gauge calibrated? 		☐ Yes   ☐  No   ☐  N/A

Date of last calibration:

C. If dry charge batteries were supplied, was electrolyte added at

least 24 hours prior to engine start-up and were batteries given a

conditioning charge? 			☐ Yes   ☐  No   ☐  N/A

D. For each test, record the following for each load condition:

| Test | Driver Speed | Suction Pressure | Discharge Pressure | Nozzle Size | Pitot Readings or Flow |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | rpm | psi | psi | inch | 1 | 2 | 3 | 4 | 5 | 6 |
| 0% |  |  |  |  | X | X | X | X | X | X |
| 25% |  |  |  |  |  |  |  |  |  |  |
| 50% |  |  |  |  |  |  |  |  |  |  |
| 75% |  |  |  |  |  |  |  |  |  |  |
| 100% |  |  |  |  |  |  |  |  |  |  |
| 125% |  |  |  |  |  |  |  |  |  |  |
| 150% |  |  |  |  |  |  |  |  |  |  |

E. For electric motor driven pumps, also record:

| Test | Voltage | Amperes |
| --- | --- | --- |
| 0% |  |  |
| 25% |  |  |
| 50% |  |  |
| 75% |  |  |
| 100% |  |  |
| 125% |  |  |
| 150% |  |  |

F. Calculate Net Pressure and Total Flow:

PNET = PDISCHARG – PSUCTION		Q= 29.83 cd2√P

| Test | Net Pressure | Pitot Readings or Flow |  |  |  |  |  | Total Flow |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 | 2 | 3 | 4 | 5 | 6 |  |
| 0% |  | X | X | X | X | X | X |  |
| 25% |  |  |  |  |  |  |  |  |
| 50% |  |  |  |  |  |  |  |  |
| 75% |  |  |  |  |  |  |  |  |
| 100% |  |  |  |  |  |  |  |  |
| 125% |  |  |  |  |  |  |  |  |
| 150% |  |  |  |  |  |  |  |  |

G. For  electric  motors  operating  at  rated  voltage  and  frequency,  is  the ampere  demand  on  each  phase  less  than  or  equal  to  the  product  of  the full load ampere rating times the allowable service factor as stamped on the motor nameplate? 			☐ Yes   ☐  No   ☐  N/A

H. For electric motors operating under varying voltage:

1. Was the product of the actual voltage and current demand on each phase

less than or equal to the product of the rated full load current times the rated

voltage times the allowable service factor? 	☐ Yes   ☐  No   ☐  N/A

2. Did the voltage stay within the range of 95% to 110% of the rated voltage

during the test? 			☐ Yes   ☐  No   ☐  N/A

I. Did engine-drive unit show no signal of overload or

stress?	 			☐ Yes   ☐  No   ☐  N/A

J. Was the governor set to properly regulate the engine speed at the rated pump speed?     				☐ Yes   ☐  No   ☐  N/A

K. Did the gear drive assembly operate without excessive objectionable noise, vibration or heating? 			☐ Yes   ☐  No   ☐  N/A

L. Was the unit started and brought up to the rated speed without interruption under discharge conditions equal to peak load? 	☐ Yes   ☐  No   ☐  N/A

M. Did the fire pump perform equal to the manufacturer’s curve within the accuracy limits of the test equipment? 	☐ Yes   ☐  No   ☐  N/A

N. Did the unadjusted performance discharge curve meet or exceed the fire protection system demand(s)? 		☐ Yes   ☐  No   ☐  N/A

O. No vibrations that could potentially damage any fire pump

components? 			☐ Yes   ☐  No   ☐  N/A

P. The fire pump preformed at all conditions without objectionable overheating of any component? 			☐ Yes   ☐  No   ☐  N/A

Q. Electric motor pumps passed phase reversal test on normal and alternate (if provided) power? 			☐ Yes   ☐  No   ☐  N/A

R. If a break tank is provided, was the refill mechanism tested 5 times and did it operate correctly? 			☐ Yes   ☐  No   ☐  N/A

Record refill rate :

S. For vertical turbine pumps taking suction from wells, is the water level capable of being recorded? 			☐ Yes   ☐  No   ☐  N/A

VI. Controller Test

A. Did the pump start at last 6 times from automatic

source? 				☐ Yes   ☐  No   ☐  N/A

B. Was each automatic starting feature tested at least

once? 				☐ Yes   ☐  No   ☐  N/A

C. Was the pump start at least 6 times manually? 	☐ Yes   ☐  No   ☐  N/A

D. Was the pump run for at least 5 minutes during each of the operations in Parts A, B, and C above? 			☐ Yes   ☐  No   ☐  N/A

(Note : An engine driver is not required to run for 5 minutes at full speed between successive starts until the cumulative cranking time of successive starts reaches 45 seconds.)

E. Were the starting operations divided between both sets of batteries for engine-driven controllers? 			☐ Yes   ☐  No   ☐  N/A

F. Electric Driven Pump Controllers

1. Were all overcurrent protective devices (including the

controller circuit breaker) selected, sized and set in accordance

with NFPA 20? 			☐ Yes   ☐  No   ☐  N/A

2. Was the fire pump started at least once from each power service and run for

at least 5 minutes? 			☐ Yes   ☐  No   ☐  N/A

3. Upon simulation of a power failure, while the pump is operating at

peak load, did the transfer switch  transfer from the normal to

the emergency source without opening overcurrent protection devices

on either line? 			☐ Yes   ☐  No   ☐  N/A

4. When normal power was restored, did retransfer from emergency to

normal power occur without overcurrent protection device devices opening

on either line? 			☐ Yes   ☐  No   ☐  N/A

5. Were at least half of the automatic and manual starts required by

Parts A and C performed with the pump connected to the alternate

source? 			☐ Yes   ☐  No   ☐  N/A

G. Were all signal conditions simulated demonstrating satisfactory

operation? 			☐ Yes   ☐  No   ☐  N/A

H. Was the pump run for at least 1 hour total during all of the

above tests? 			☐ Yes   ☐  No   ☐  N/A

I. For engines with ECM fuel management systems, primary and alternate

ECM passed function test? 		☐ Yes   ☐  No   ☐  N/A

VII. Information For Owner

Was the owner given all of the following? 	☐ Yes   ☐  No   ☐  N/A

A. A manual explaining the operation of all the components.

B. Instructions for routine maintenance and repairs.

C. Parts list and parts identification.

D. List of recommended spare parts and lubricant to keep on hand.

E. Schematics electrical drawings of controllers, transfer switch, and alarm panels.

F. Manufacturer’s certified shop test curve or acceptance test curve.

VIII. Tester Information

Tester :

Company :

Company Address :

I state that the information on this form is correct at the time and place of my test, and that all equipment tested was left in operational condition upon completion of this test except as noted in the comments section below.

Signature of Tester:

Date :

License or Certification Number (if Applicable):

IX. Comments

(Any “No” answers test failures, or other problems must be explained here.)

Pump Test Result

Pressure (psi, fill in scale)

Amperes (for electric  driven pumps, fill in scale)

|  |  |  |  |  |  |  |  |  |  | Flow (gpm, fill in scale) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |