| PROJECT NAME: |  |  | DRAWING NO. |  |  |  |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. | QUESTIONS |  |  | ORIGINATOR |  |  | CHECKER |  |  |  |
|  |  |  |  | N/A | YES | NO | N/A | YES |  | NO |
| Drawing Presentation |  |  |  |  |  |  |  |  |  |  |
|  | All lines, symbols, legends, abbreviations and text are legible and in compliance with Project CAD procedures. |  |  |  |  |  |  |  |  |  |
|  | Fields in the drawing title block are consistent with the project Procedure. |  |  |  |  |  |  |  |  |  |
|  | Drawing notes are complete & agree with information on the drawings & details. |  |  |  |  |  |  |  |  |  |
|  | Holds & revisions are correctly marked. |  |  |  |  |  |  |  |  |  |
|  | Match lines verified with matching drawings and found correct with respect to circuit continuity and drawing numbers. |  |  |  |  |  |  |  |  |  |
| Codes/Standards/Project Requirements |  |  |  |  |  |  |  |  |  |  |
|  | The system design and the selection of the equipment’s shall comply with the applicable Code, International and Saudi standard, local Government Regulation and Project Specification. |  |  |  |  |  |  |  |  |  |
|  | Verify the equipment tag/identification numbers, dimensions, locations, etc. with project standards/vendor documents. |  |  |  |  |  |  |  |  |  |
|  | Feeder rating and cable sizes for loads as per Project specifications, Design criteria, Manufacturer’s catalogues and applicable codes and standards. |  |  |  |  |  |  |  |  |  |
|  | All protections and metering arrangement have been shown as per project specifications/design criteria. |  |  |  |  |  |  |  |  |  |
|  | Breaker rating, Contactor rating, starter rating & fuse rating in accordance with Project Specifications/design criteria. |  |  |  |  |  |  |  |  |  |
| Reference Information |  |  |  |  |  |  |  |  |  |  |
|  | Check to ensure general notes include reference to applicable Codes, Standards and Project Specifications/Supplier submittals. |  |  |  |  |  |  |  |  |  |
|  | Do SLD specifies the type of enclosure and switchgear assemblies? |  |  |  |  |  |  |  |  |  |
|  | Do the SLD specify the requirement regarding ARC Ventilation System? |  |  |  |  |  |  |  |  |  |
|  | Are the layout provided with the detail of the components (Main Bus, Ground bus, Instrument transformers (CT’s & PT’s), Metering’s, relays, surge protection devices, etc.)? |  |  |  |  |  |  |  |  |  |
|  | Check for correctness and completeness of applicable documents, reference drawings and legend list. |  |  |  |  |  |  |  |  |  |
|  | List and verify any special/specific requirements by others (Sub-Contractors, Vendors, etc.). |  |  |  |  |  |  |  |  |  |
| Design |  |  |  |  |  |  |  |  |  |  |
|  | Have the feeders (incoming, outgoing, bus coupling or Tie Breaker, etc.) verified per load list/equipment list report? Verify all loads are shown on drawings. |  |  |  |  |  |  |  |  |  |
|  | Does Single Line Diagram (SLD) provide the details of the contract and or ownership boundaries. |  |  |  |  |  |  |  |  |  |
|  | Are the Feeder sizes and cable sizes verified for proper voltage drop/ continuous & short circuit current rating (kA) per Project Specifications/ design criteria/Manufacturer’s catalogues? Check against project cable sizing calculations. |  |  |  |  |  |  |  |  |  |
|  | Are the feeder sizes verified for the loads indicated per Equipment list, Project Specifications and applicable codes and standards? |  |  |  |  |  |  |  |  |  |
|  | Have the electrical equipment numbers verified against component numbering system applicable for the project? |  |  |  |  |  |  |  |  |  |
|  | Are bus designations, bus voltage, ampere ratings, short circuit ratings and configuration (3ph. 3 wire or 4 wire, etc.) identified & verified for all buses / bus sections? |  |  |  |  |  |  |  |  |  |
|  | Does Single line diagram provide the details of Medium Voltage Switch such as Fuses Rating, Type and looping arrangements? |  |  |  |  |  |  |  |  |  |
|  | Have the Single Line Diagram prepared by consideration of appropriate Safety provisions for equipment / bus isolation, safety grounding, Lock Out Tag Out (LOTO). maintenance, testing. |  |  |  |  |  |  |  |  |  |
|  | Are the equipment continuous & short circuit current capability, equipment protections, BIL, Voltage, frequency values verified against scope document, calculations and system characteristics? |  |  |  |  |  |  |  |  |  |
|  | Are the protection philosophy and redundancy in line with the design and the project requirements? |  |  |  |  |  |  |  |  |  |
|  | Have the power protection for incomers and tie-in Circuit Breakers compliant with the Electrical Utility Supplier (SEC) requirements? |  |  |  |  |  |  |  |  |  |
|  | Are SLD prepared against Electrical System Calculations for bus/breaker/ transformer sizes/fault ratings (Over current protection, short circuit protection, earth fault protection)? |  |  |  |  |  |  |  |  |  |
|  | Check that following information is provided for electrical equipment and is accurate: - Transformers: Identification no., MVA/ KVA, Voltage ratio, taps, %Z, connection, phasors, Cooling, grounding, location - Motors: Identification no., HP/ KW, Voltage, Hz, RPM, location. |  |  |  |  |  |  |  |  |  |
|  | Verify following parameters for instrument transformers for Metering/ Protection: CT: Identification No., Ratio, VA, Accuracy Class, connection, grounding requirement, polarity markings, location PT: Identification No, Ratio, VA, Accuracy Class, Connection, grounding requirement, location Revenue metering CT/ PT shall receive special attention on accuracy/ limit factor. Verify quantity of instrument transformers. |  |  |  |  |  |  |  |  |  |
|  | Are PT and CT ratios shown correctly, indicate 1ph or 3ph, quantity, Class and VA burden? |  |  |  |  |  |  |  |  |  |
|  | Have SLD describes or the scheme considered Switchgear/MCC - Arc Containment (or Arc Resistant) ratings including degree of internal separation IEC Form 1, 2a, 2b… 4a, 4b)? - If applicable. |  |  |  |  |  |  |  |  |  |
|  | Are CT’s and PT’s located in appropriate location to ensure the accuracy and also to make the ‘Provisions for performance testing”, if required? |  |  |  |  |  |  |  |  |  |
|  | Do SLD provides the information regarding Bus Transfer methods, Dead Bus, Fast transfer, Synchronized, Operator initiated, Automatic, etc.? |  |  |  |  |  |  |  |  |  |
|  | Have SLD prepared or considered the Phase Rotation Diagram (Phase Sequence), Diagram showing phase relationship of all systems voltages used from highest Grid / Utility through lowest system voltage? |  |  |  |  |  |  |  |  |  |
|  | Do SLD describe the provision for ‘Computer input requirements’? |  |  |  |  |  |  |  |  |  |
|  | Do the scheme considered the ‘Safety Interlocking’? |  |  |  |  |  |  |  |  |  |
|  | Check for spare feeders as per design guides/project's specifications and standards. |  |  |  |  |  |  |  |  |  |
|  | Are the layouts provide the details of Earthing System? |  |  |  |  |  |  |  |  |  |
| Others |  |  |  |  |  |  |  |  |  |  |
|  | Notes clarifying operational/ functional characteristics shall be listed. Any assumptions shall be clearly listed. |  |  |  |  |  |  |  |  |  |
|  | Compare against vendor prints to verify all spaces & spares are shown. Verify compliance to Project criteria’s and identify battery limits clearly defined for the packaged equipment. |  |  |  |  |  |  |  |  |  |
| No. | Reviewer's Comments (against each SLD) | Resolution |  |  |  |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |  |  |  |