| PROJECT NAME: |  |  |  | DISCIPLINE: |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| EQUIPMENT TYPE: STANDARD MECHANICAL DESIGN DELIVERABLES |  | EQUIPMENT TAG: |  | EQUIPMENT LOCATION: |  |  |  |
| No. | QUESTIONS |  |  |  | ORIGINATOR |  |  |
|  |  |  |  |  | N/A | YES | NO |
| HVAC SYSTEM DELIVERABLES |  |  |  |  |  |  |  |
| 1 | HVAC Plan and Drawing which includes the following; |  |  |  |  |  |  |
|  | - General Notes, Legends, and Abbreviation |  |  |  |  |  |  |
|  | - Drawing List |  |  |  |  |  |  |
|  | - Standard Detail Drawings |  |  |  |  |  |  |
|  | - Ducting Floor Plan Layout Drawings showing Uniform Friction Losses (UFL) and air velocity. UFL is shown to ensure oversizing is avoided and velocity to avoid excessive noise generation. |  |  |  |  |  |  |
|  | - Chilled/condenser Water or Refrigerant Piping Floor Plan Layout Drawings. UFL and fluid velocity is shown to ensure oversizing is avoided and velocity to avoid excessive noise generation. |  |  |  |  |  |  |
|  | - Steam and Process Hot Water Piping Floor Plan Lay-out Drawings. Fluid velocity is shown to ensure excessive sizing is avoided. |  |  |  |  |  |  |
|  | - Plant Room Lay-out Drawing |  |  |  |  |  |  |
|  | - External/Underground mechanical piping services drawings (as applicable) |  |  |  |  |  |  |
|  | - Single Line Diagram for chilled water distribution systems. UFL and velocity is indicated. |  |  |  |  |  |  |
|  | - Single Line Diagram for air distribution systems. UFL and velocity is indicated. |  |  |  |  |  |  |
|  | - Single Line Diagram for steam systems. Fluid velocity is indicated. |  |  |  |  |  |  |
|  | - Equipment Schedule |  |  |  |  |  |  |
|  | - BMS Process and Instrumentation Diagram for equipment, water and air distribution system |  |  |  |  |  |  |
|  | - BMS Sequence of Operation for equipment, water and air distribution system |  |  |  |  |  |  |
|  | - Based on Psychrometric Analysis, the AHU internal arrangement for cooling coil, humidifier, dehumidifier, and heating coil (as applicable) |  |  |  |  |  |  |
| 2 | Calculations which includes; |  |  |  |  |  |  |
|  | - Cooling and heating load output from Hevacomp, HAP, TRACE, and other reputable HVAC software |  |  |  |  |  |  |
|  | - Airflow calculation for application with minimum ACH (Air change per Hour) requirement- e.g. Healthcare, Laboratories, cleanrooms, semi-conductors, etc. |  |  |  |  |  |  |
|  | - Psychrometric Process and calculation for cooling, heating, humidification, and dehumidification- applicable for complex HVAC system (healthcare, medicine factory, paper factory, etc.) Centralized AHU process, with minimal allowed precise room temperature/RH fluctuations, low temperature or %RH application, and dual external seasons (hot and cold ambient conditions). |  |  |  |  |  |  |
|  | - Fresh Air requirements for Indoor Air Quality and Building Pressurization |  |  |  |  |  |  |
|  | - Exhaust requirements for toilets, kitchen, isolation, etc. |  |  |  |  |  |  |
|  | - HVAC Equipment calculation which includes: |  |  |  |  |  |  |
|  | - Cooling capacity for AHU, FAHU, and FCU |  |  |  |  |  |  |
|  | - Heating capacity for AHU, FAHU, and FCU as applicable |  |  |  |  |  |  |
|  | - Energy Recovery Unit for AHU and HRF (Heat Recovery Fan) |  |  |  |  |  |  |
|  | - AHU Fan flowrate, ESP (External Static Pressure), and consumed power based on TSP (Total Static Pressure). |  |  |  |  |  |  |
|  | - Supply/Exhaust Fan flowrate, ESP (External Static Pressure), and consumed power. |  |  |  |  |  |  |
|  | - Chilled Water Pump flowrate and head |  |  |  |  |  |  |
|  | - Condenser Water Pump flowrate and head |  |  |  |  |  |  |
|  | - Cooling Tower Capacity and CT Fan flowrate/Power Consumption |  |  |  |  |  |  |
|  | - Process Heating Circulating Pump flowrate and head |  |  |  |  |  |  |
|  | - Chiller nominal capacity based on target de-rating factor |  |  |  |  |  |  |
|  | - Steam Boiler capacity and pressure head |  |  |  |  |  |  |
|  | - Boiler Feed Water tank and pump capacity |  |  |  |  |  |  |
|  | - Condensate Recovery Unit tank capacity and pump capacity/head |  |  |  |  |  |  |
|  | - Steam Pressure Reducing Station sizing & Cv value considered for Steam PRV |  |  |  |  |  |  |
|  | - Other equipment calculation (e.g. VAV, CAV, etc.) |  |  |  |  |  |  |
| 3 | Particular Specification for BMS to include Data Point Schedule for mechanical and electrical systems. |  |  |  |  |  |  |
| 4 | General Project Specification for HVAC Systems, Equipment, piping & accessories, ducting and accessories. |  |  |  |  |  |  |
| MECHANICAL FIRE AND LIFE SAFETY SYSTEM DELIVERABLES |  |  |  |  |  |  |  |
| 1 | *Mechanical Fire and Life Safety Plan to include: |  |  |  |  |  |  |
|  | - Staircase Pressurization Single Line Diagram and Sequence of Operation |  |  |  |  |  |  |
|  | - Lift Lobby or Lift Shaft Pressurization Single Line Diagram and Sequence of Operation |  |  |  |  |  |  |
|  | - Atrium Smoke Extraction System Diagram and Sequence of Operation |  |  |  |  |  |  |
|  | - Zone Smoke Control System Diagram and Sequence of Operation |  |  |  |  |  |  |
|  | - Car Parking Smoke Extraction System by Jet Fans or conventional fire rated ducting system with Sequence of Operation. |  |  |  |  |  |  |
|  | - Equipment and ducting Schedule with fire rating requirements. |  |  |  |  |  |  |
| 2 | Calculation which includes: |  |  |  |  |  |  |
|  | - Air flowrate required for Stair Pressurization based on considered number of open doors, differential pressure across the doors, and air leakage. |  |  |  |  |  |  |
|  | - Air flowrate required for lift lobby or lift shaft pressurization based on differential pressure across the doors and air leakage. |  |  |  |  |  |  |
|  | - Air flowrate required for Atrium smoke extraction based on fire load, heat release rate, smoke reservoir details, and sprinklered or unsprinklered building. |  |  |  |  |  |  |
|  | - Air flowrate required for Zoned Smoke Control System based on fire load, heat release rate, smoke reservoir detail, sprinklered or unsprinklered building, and differential pressure across doors. |  |  |  |  |  |  |
|  | - Airflow calculation for Car Park Smoke Control Management and CFD (Computational Fluid Dynamics) Analysis for Jet Fan System. |  |  |  |  |  |  |
|  | - Fan External Static Pressure calculation for Staircase Pressurization, Lift Lobby or Lift Shaft Pressurization, Zone Smoke Control (dedicated system) and Atrium Smoke Extraction. |  |  |  |  |  |  |
|  | - Fan Motor absorbed power for FLS Fans based on item f. |  |  |  |  |  |  |
|  | - Fan External and Total Static Pressure calculation for Zone Smoke Control (non-dedicated system) and fan motor power requirement. |  |  |  |  |  |  |
| 3 | General Project Specification for Mechanical FLS Systems, Equipment, ducting and accessories. |  |  |  |  |  |  |
| PLUMBING DELIVERABLES |  |  |  |  |  |  |  |
| 1 | Plumbing Plans and Drawings to include: |  |  |  |  |  |  |
|  | - General Notes, Legends, and Abbreviation |  |  |  |  |  |  |
|  | - Drawing List |  |  |  |  |  |  |
|  | - Standard Detail Drawings |  |  |  |  |  |  |
|  | - Domestic Cold and Hot Water Floor Plan Lay-out Drawings. Uniform Friction Loss (UFL) is shown to ensure oversizing is avoided, and velocity to avoid excessive noise generation. |  |  |  |  |  |  |
|  | - Pump Room Lay-out Drawing |  |  |  |  |  |  |
|  | - Drainage Floor Plan Lay-out Drawings |  |  |  |  |  |  |
|  | - External/Underground Cold Water services drawings |  |  |  |  |  |  |
|  | - External/Underground Drainage services drawings |  |  |  |  |  |  |
|  | - Single Line Diagram for domestic cold, hot water, and hot water circulation systems. UFL and velocity are indicated. |  |  |  |  |  |  |
|  | - Drainage System Single Line Diagram. Fixture Unit (FU) or Discharge Unit (DU) is indicated to ensure oversizing is avoided. |  |  |  |  |  |  |
|  | - Equipment Schedule |  |  |  |  |  |  |
| 2 | Calculation which includes: |  |  |  |  |  |  |
|  | - Cold and hot water storage |  |  |  |  |  |  |
|  | - Fixture Unit (FU) or Loading Unit (LU) and Discharge Unit (DU) summation for domestic water pipe/drainage sizing and pump (booster, sewage, and ejector) flowrate determination |  |  |  |  |  |  |
|  | - Pump head calculation and power requirements |  |  |  |  |  |  |
| 3 | General Project Specification for Plumbing Systems, Equipment, piping and accessories. |  |  |  |  |  |  |
| Fire Protection, Sprinkler and Standpipe System Deliverables |  |  |  |  |  |  |  |
| 1 | Fire Sprinkler Plans and Drawings to include: |  |  |  |  |  |  |
|  | - General Notes, Legends, and Abbreviation |  |  |  |  |  |  |
|  | - Drawing List |  |  |  |  |  |  |
|  | - Standard Detail Drawings |  |  |  |  |  |  |
|  | - Fire Sprinkler, Stand-pipe, Fire Hose Cabinet, Fire Extinguishers, Pre-action (as applicable), and Clean Agent Floor Plan Lay-out Drawings |  |  |  |  |  |  |
|  | - Fire Pump Room Lay-out Drawing |  |  |  |  |  |  |
|  | - Hydrants and External/Underground Fire Water Services drawings |  |  |  |  |  |  |
|  | - Single Line Diagram for Sprinkler and Stand-pipe System |  |  |  |  |  |  |
|  | - Equipment Schedule |  |  |  |  |  |  |
| 2 | Calculation which includes: |  |  |  |  |  |  |
|  | - Fire water storage based on hazard classification |  |  |  |  |  |  |
|  | - Pump head calculation |  |  |  |  |  |  |
|  | - Power requirements |  |  |  |  |  |  |
|  | - Hydraulic Calculation for pipe sizing if Pipe Schedule Method is not used. |  |  |  |  |  |  |
|  | - Clean Agent Capacity calculation |  |  |  |  |  |  |
| 3 | General Project Specification for Fire Sprinkler Systems, equipment, piping and accessories. |  |  |  |  |  |  |
| **FIRE DETECTION AND ALARM SYSTEM CAUSE AND EFFECT MATRIX |  |  |  |  |  |  |  |
| 1 | The C&E Matrix (Table) shall be prepare by the Electrical Engineering Division in coordination with the FLS (Fire and Life Safety) Consultant, architect, and mechanical design engineer. |  |  |  |  |  |  |
|  | * Mechanical FLS Equipment and ducting layout is normally included in HVAC ducting plan. |  |  |  |  |  |  |
|  | **Only serves as note for multi-discipline coordination. |  |  |  |  |  |  |
| No. | Reviewer's Comments (against each SLD) |  | Resolution |  |  |  |  |
| Originator's Name / Signature and Date: |  |  | Checker's Name / Signature and Date: |  |  |  |  |