| PROJECT NAME: |  |  | U/G UTILITY LAYOUT DWG NO. |  |  |  |  | REV. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. | QUESTIONS |  | ORIGINATOR |  |  | CHECKER |  |  |
|  |  |  | N/A | YES | NO | N/A | YES | NO |
| 1 | Was the correct drawing template used (title block and borders)? |  |  |  |  |  |  |  |
| 2 | Was the latest background used? |  |  |  |  |  |  |  |
| 3 | Does the title block show the reason for issue/revision, and is the associated revision letter or number appropriate and consistent with Project Procedures? |  |  |  |  |  |  |  |
| 4 | Is the layout drawing number in accordance with Project Procedures? |  |  |  |  |  |  |  |
| 5 | Have all outstanding change papers (e.g., DCNs, FCDs, NCRs, etc.) been incorporated and noted as such in the title block? |  |  |  |  |  |  |  |
| 6 | Is there an Intellectual Property (IP)/Disclaimer Statement on the drawing? |  |  |  |  |  |  |  |
| 7 | Are the symbols for piping, valves, and any other specialty components in accordance with the Project's standard symbols and legends? |  |  |  |  |  |  |  |
| 8 | Are the line tag numbers, sizes, materials, and configuration consistent with the latest version of the associated P&ID? |  |  |  |  |  |  |  |
| 9 | Are there any markups on the master red-lined P&ID (showing pending P&ID changes) that need to be incorporated into the pipe layout on this drawing? |  |  |  |  |  |  |  |
| 10 | Are there any changes (e.g., branch take-off order) that need to be marked on the master red-lined P&ID to reflect the "as-built" configuration on this layout drawing? |  |  |  |  |  |  |  |
| 11 | Are any specialty fittings clearly identified (e.g., reducing tee, 45° elbow, long-radius vs. short radius 90° elbow, etc.)? |  |  |  |  |  |  |  |
| 12 | Are valve boxes shown to allow access to any valves located below grade and are reach rods or extension stems show on such valves? |  |  |  |  |  |  |  |
| 13 | If back-flow preventers or check valves are required in the underground lines, is the orientation (direction of flow) of each valve correctly shown? |  |  |  |  |  |  |  |
| 14 | Are sufficient dimensions shown to precisely locate and describe the pipe configuration (with dimensions indicated for all horizontal and vertical runs)? |  |  |  |  |  |  |  |
| 15 | Is the pipe sloped properly (per the applicable plumbing code) and to allow for drainage if required? |  |  |  |  |  |  |  |
| 16 | Are field welds/fusions/connections shown and are they in appropriate locations (outside the bend clamp length where applicable for flexible, non-metal pipe)? |  |  |  |  |  |  |  |
| 17 | Are individual spool lengths (between field welds/fusions/ connections) appropriate for transport to the project site? |  |  |  |  |  |  |  |
| 18 | Do valve end-to-end dimensions match the appropriate supplier drawings? |  |  |  |  |  |  |  |
| 19 | Is the direction of flow indicated (if not obvious) for all lines? |  |  |  |  |  |  |  |
| 20 | Have Constructability requirements been considered? |  |  |  |  |  |  |  |
| 21 | Have Operability requirements been considered? |  |  |  |  |  |  |  |
| 22 | Has Accessibility for repair, maintenance, and inspection been considered? |  |  |  |  |  |  |  |
| 23 | Is cathodic protection indicated if required? |  |  |  |  |  |  |  |
| 24 | Has an interference check been performed and have clashes been resolved? |  |  |  |  |  |  |  |
| 25 | Were all the match lines checked on this drawing and found to be correct? |  |  |  |  |  |  |  |
| 26 | Do the line sizes and material/ratings on this drawing match other drawings at the interfaces (for all off-page connector match points)? |  |  |  |  |  |  |  |
| 27 | Is the routing optimized to reduce total installed cost (e.g., minimize pipe lengths)? |  |  |  |  |  |  |  |
| 28 | Is the routing optimized to minimize the final depth for collection of gravity floor drains (which may require splitting into parallel branches to avoid re-pumping)? |  |  |  |  |  |  |  |
| 29 | Are pipe bends use in lieu of fittings where appropriate to reduce friction losses? |  |  |  |  |  |  |  |
| 30 | If there are multiple lines in a given trench, is each line located at the correct elevation (e.g., is the potable water line located above the sanitary sewer line)? |  |  |  |  |  |  |  |
| 31 | If there are multiple lines in a given trench, has the applicable separation criteria been followed (to follow a code or allow for movement after initial installation)? |  |  |  |  |  |  |  |
| 32 | Does the system design comply with applicable codes, standards, and regulatory requirements? |  |  |  |  |  |  |  |
| 33 | Does the system design comply with the applicable Project Mechanical Design Criteria, Project Scope Book, or any other Project Design Basis Documents? |  |  |  |  |  |  |  |
| 34 | Are the notes appropriate and are they marked in applicable places on the drawing? |  |  |  |  |  |  |  |
| 35 | Are references made to the associated P&ID and any applicable Standard Details where required to provide additional clarity? |  |  |  |  |  |  |  |
| 36 | Has appropriate interdisciplinary and intradepartmental coordination of the drawing been completed? |  |  |  |  |  |  |  |
| 37 | Has the Originator of the drawing resolved coordination comments and incorporated changes where required? |  |  |  |  |  |  |  |
| 38 | If required, has the drawing been stamped by a registered Professional Engineer? |  |  |  |  |  |  |  |
| 39 | On drawings "Issued for Construction" (Rev. 000 or higher), have areas of the drawing with incomplete designs or preliminary information been placed on hold? |  |  |  |  |  |  |  |
| 40 | If the drawing is being revised, are changes clearly shown (e.g., using clouds, revision triangles, or notes in the revision line of the title block)? |  |  |  |  |  |  |  |
| 41 | If the drawing is being revised, are all previous revision markings (clouds or triangles) removed? |  |  |  |  |  |  |  |
| 42 | Is the north arrow indicated in the drawings? |  |  |  |  |  |  |  |
| No. | Reviewer's Comments (against each SLD) | Resolution |  |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |  |